## 05_28_2024
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/28/2024
Plant Data Conversion |  |  |  |  | Summary Table
Belt No. | A4 | Poly Loading (lb) | 448.8288 |  |  |  |  | batch testing
Poly Ratio | 0.165 | Floc Poly Flow (gpm) | 14.949 |  |  | unit | Plant | OPD | EPD
Sludge Flow (gpm) | 90.6 | Poly Floc Flow (mgd) | 0.021527 |  | BFP TS | %TS | 3.5085
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.13046 |  | Polymer ratio setting | - | 0.165 | 0.165 | 0.165
SBT3 TS % LAB_TSPCT_J04 | 6.1 | Calculated BFP TS (%) | 3.7289 |  | Polymer dose | lb/tonTS | 21.7109 | 26.6031 | 23.8997
BFP TS % | 3.7999 | BFP Sludge Loading (dtpd) | 20.2865 |  | Cake TS | %TS | 28.6677 | 26.0874 | 29.7472
DIG SLDG FLOW FROM SBT (gpm) | 552 | Plant Polydose (Ib/ton) - method 1 | 22.1245 |  | Filtrate TSS | mg TSS/L | 600 | 810 | 705
DIL WTR FLOW TO BFP (gpm) | 351 | Plant Polydose (Ib/ton) - method 2 | 21.7109
Assumptions and Constants:
1 g = | 0.0022046 | lb
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches
Cup Area: | 0.0079059 | m2
Aiming for 0.80 kg of DS per m2 of cup area
Cup Loading | 6.3247 | grams of DS
Assuming | 3.5 | TS in sludge
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m
Calculation
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g)
1 | 17 | 3.8 | 504.72 | 65.2098 | 67.24 | 1.98 | 65.26 | 17.0131 | 206.64 | 408.48 | 351.96 | 786.95 | 100 | 145.32 | 378.47 | 12.1285 | 52.1477
2 | 19 | 3.8 | 503.8 | 72.7487 | 73.85 | 2.11 | 71.74 | 18.7366 | 205.76 | 407.97 | 353.89 | 795.38 | 100 | 148.13 | 387.41 | 12.0258 | 52.5928
3 | 21.5 | 3.8 | 501.37 | 81.9238 | 83.5 | 1.9 | 81.6 | 21.415 | 159.38 | 412.95 | 301.78 | 785.76 | 100 | 142.4 | 372.81 | 11.8242 | 53.4899
4 | 24 | 3.8 | 502.76 | 91.7034 | 92.92 | 1.6 | 91.32 | 23.8997 | 401.68 | 399.01 | 540.86 | 759.18 | 100 | 139.18 | 360.17 | 11.5379 | 54.8168
5 | 26.5 | 3.8 | 500.98 | 100.8973 | 102.91 | 1.62 | 101.29 | 26.6031 | 509.76 | 686.52 | 684.82 | 1047 | 100 | 175.06 | 360.48 | 9.6698 | 65.4069
6 | 29 | 3.8 | 504.06 | 111.0948 | 112.85 | 1.22 | 111.63 | 29.1397 | 443.26 | 361.64 | 571.18 | 741 | 100 | 127.92 | 379.36 | 12.3371 | 51.2659
CST Table | [16 empty] | 0
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 121.6 | 47.9667 |  |  | 128.9 | 114.3 |  | 42.7 | 54.6 | 46.6
2 | 114.4333 | 45.05 | 91.6 | 133 | 118.7 |  |  | 41.8 |  | 48.3
3 | 55.6 | 43.9333 |  | 52.7 | 58.5 | 65 |  | 42.9 | 39.7 | 49.2 | [9 empty] | Summary - 05 - 03 - 2024 | [7 empty] | Trend over time
4 | 49.2 | 39.8 | 54.4 | 44 |  |  | 67 | 37.7 | 37.1 | 44.6
5 | 40.55 | 34.05 | 42.1 | 41.7 | 39.4 |  |  | 33.1 |  | 35 |  | 43.7
6 | 39.8333 | 24.0333 | 39 | 41 | 39.5 |  |  | 28.7 | 22.4 | 21
Target table
TSS - VSS | [23 empty] | BFP TS | Filtrate TS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%) | [7 empty] | Unit | % | mg TSS/L
1 | 1.0936 | 1.0981 | 10 | 10 | 1.105 | 1.1105 | 1 | 1.14 | 1.24 | 1.19 | 1.0952 | 1.1002 | 980 | 1030 | 1005 | [8 empty] | 3 - 3.9 | <= 812
2 | 1.1015 | 1.1064 | 10 | 10 | 1.1126 | 1.1182 | 1 | 1.11 | 1.18 | 1.145 | 1.1024 | 1.1084 | 1020 | 980 | 1000
3 | 1.1183 | 1.12 | 10 | 10 | 1.127 | 1.131 | 1 | 0.87 | 1.1 | 0.985 | 1.1185 | 1.122 | 850 | 900 | 875 | [5 empty] | Summary Table
4 | 1.1297 | 1.1231 | 10 | 10 | 1.1364 | 1.1305 | 1 | 0.67 | 0.74 | 0.705 | 1.1303 | 1.1242 | 610 | 630 | 620 | [8 empty] | batch testing
5 | 1.1131 | 1.1171 | 10 | 10 | 1.1213 | 1.1251 | 1 | 0.82 | 0.8 | 0.81 | 1.1134 | 1.1179 | 790 | 720 | 755 | [6 empty] | unit | Plant | OPD | EPD
6 | 1.1061 | 1.1164 | 10 | 10 | 1.1103 | 1.1207 | 1 | 0.42 | 0.43 | 0.425 | 1.1065 | 1.1169 | 380 | 380 | 380
Plant Filterate | 1.102 | 1.1056 | 10 | 10 | 1.1079 | 1.1134 | 1 | 0.59 | 0.78 | 0.685 | 1.1022 | 1.1071 | 570 | 630 | 600 | [5 empty] | BFP TS | %TS | 3.5085
. | [20 empty] | Polymer ratio setting | vol/vol | 0.165 | 0.165 | 0.165
[21 empty] | Polymer dose | lb/tonTS | 21.7109 | 26.6031 | 23.8997
TS - VS | [20 empty] | Cake TS | %TS | 28.6677 | 26.0874 | 29.7472
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%) | [6 empty] | Filtrate TSS | mg TSS/L | 600 | 810 | 705
1 | 0.9859 | 0.9891 | 5.07 | 5.1332 | 2.1986 | 2.2118 | 29.6932 | 29.5046 | 29.5989 | 1.4211 | 1.428 | 15.3353 | 15.2692 | 15.3023
2 | 0.9919 | 0.9909 | 5.1155 | 5.1928 | 2.174 | 2.1693 | 28.6667 | 28.0445 | 28.3556 | 1.4224 | 1.4178 | 14.6926 | 14.472 | 14.5823
3 | 1.0131 | 0.9908 | 5.058 | 5.504 | 2.152 | 2.3096 | 28.1564 | 29.221 | 28.6887 | 1.431 | 1.4774 | 14.2546 | 15.1199 | 14.6873
4 | 0.9809 | 0.9809 | 5.1914 | 5.1421 | 2.2377 | 2.2145 | 29.8492 | 29.6453 | 29.7472 | 1.4405 | 1.4358 | 15.3562 | 15.1436 | 15.2499
5 | 0.9794 | 0.9999 | 5.2653 | 5.1175 | 2.1164 | 2.0559 | 26.5289 | 25.646 | 26.0874 | 1.3894 | 1.3804 | 13.8074 | 13.1998 | 13.5036
6 | 0.9806 | 0.9845 | 5.1728 | 5.0518 | 2.2263 | 2.1789 | 29.7147 | 29.3659 | 29.5403 | 1.4311 | 1.4147 | 15.3727 | 15.1273 | 15.25
Plant Cake | 0.9868 | 0.9974 | 5.2389 | 5.0126 | 2.2032 | 2.1509 | 28.607 | 28.7283 | 28.6677 | 1.4345 | 1.425 | 14.6729 | 14.4815 | 14.5772
Sludge | 1.0107 | 1.0055 | 5.2604 | 5.0626 | 1.1589 | 1.1487 | 3.4873 | 3.5296 | 3.5085 | 1.0619 | 1.0559 | 1.844 | 1.8331 | 1.8385
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Note: Based on Sludge | Ave | Diff | Tolerance (%) | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%)
17.0131 | 47.9667 | 121.6 | 29.5989 | 1190 | 47.9667 | 0 | 20 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 121.6 | 0 | 20 | 2 | 26.6031 | 26.0874 | 810 | 26.6031 | 26.0874 | 810 |  | 29.5989 | 0 | 20 | 2 | 18.7366 | #N/A | #N/A | 812 | #N/A |  | #N/A | 23.8997 | 29.7472 | 705 | yes |  | 21.7109 | 28.6677 | 600 | 3.5085
18.7366 | 45.05 | 114.4333 | 28.3556 | 1145 | 46.5083 | 6.0806 | 20 | 2 | [8 empty] | 118.0167 | 5.8936 | 20 | 2 | [7 empty] | 28.9772 | 4.2006 | 20 | 2
21.415 | 43.9333 | 55.6 | 28.6887 | 985 | 44.4917 | 5.5366 | 20 | 2 | [8 empty] | 85.0167 | 52.888 | 20 | 2 | [7 empty] | 28.5221 | 0.99575 | 20 | 2
23.8997 | 39.8 | 49.2 | 29.7472 | 705 | 41.8667 | 10.545 | 20 | 2 | [8 empty] | 52.4 | 42.129 | 20 | 2 | [7 empty] | 29.218 | -4.2953 | 20 | 2
26.6031 | 34.05 | 40.55 | 26.0874 | 810 | 36.925 | 18.6704 | 20 | 2 | [8 empty] | 44.875 | 22.6145 | 20 | 1 | [7 empty] | 27.9173 | 10.7144 | 20 | 2
29.1397 | 24.0333 | 39.8333 | 29.5403 | 425 | 29.0417 | 34.9131 | 20 | 2 | [8 empty] | 40.1917 | 11.2349 | 20 | 2 | [7 empty] | 27.8139 | -5.8135 | 20 | 2
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on D32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sub-sample weight
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 readings
Note on D49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on I40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 reading Extra slots are given for outliers
OPD
EPD

## 05_21_2024
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/21/2024
Plant Data Conversion |  |  |  |  | Summary Table
Belt No. | A3 | Poly Loading (lb) | 415.0428 |  |  |  |  | batch testing
Poly Ratio | 0.177 | Floc Poly Flow (gpm) | 13.8237 |  |  | unit | Plant | OPD | EPD
Sludge Flow (gpm) | 78.1 | Poly Floc Flow (mgd) | 0.019906 |  | BFP TS | %TS | 3.7999
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11246 |  | Polymer ratio setting | - | 0.177 | 0.177 | 0.177
SBT3 TS % LAB_TSPCT_J04 | 6.1 | Calculated BFP TS (%) | 3.4892 |  | Polymer dose | lb/tonTS | 25.9531 | 32.7416 | 23.6205
BFP TS % | 3.41 | BFP Sludge Loading (dtpd) | 16.3637 |  | Cake TS | %TS | 28.9719 | 29.7349 | 32.8894
DIG SLDG FLOW FROM SBT (gpm) | 282 | Plant Polydose (Ib/ton) - method 1 | 25.3636 |  | Filtrate TSS | mg TSS/L | 580 | 335 | 835
DIL WTR FLOW TO BFP (gpm) | 211 | Plant Polydose (Ib/ton) - method 2 | 25.9531
Assumptions and Constants:
1 g = | 0.0022046 | lb
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches
Cup Area: | 0.0079059 | m2
Aiming for 0.80 kg of DS per m2 of cup area
Cup Loading | 6.3247 | grams of DS
Assuming | 3.5 | TS in sludge
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m
Calculation
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g)
1 | 19.5 | 3.41 | 500.54 | 66.5668 | 70.28 | 1.98 | 68.3 | 20.0077 | 206.78 | 409.17 | 347.93 | 779.21 | 100 | 141.15 | 370.04 | 10.8669 | 58.2019
2 | 23 | 3.41 | 503.13 | 78.9209 | 83.55 | 2.5 | 81.05 | 23.6205 | 205.82 | 408.9 | 347.35 | 782.64 | 100 | 141.53 | 373.74 | 10.6924 | 59.1517
3 | 26 | 3.41 | 509.78 | 90.3942 | 97.51 | 2.74 | 94.77 | 27.2586 | 159.42 | 408.25 | 295.74 | 827.41 | 100 | 136.32 | 419.16 | 11.7169 | 53.9794
4 | 28.5 | 3.41 | 506.6 | 98.4678 | 103.21 | 1.7 | 101.51 | 29.3805 | 401.84 | 359.01 | 550.82 | 771.74 | 100 | 148.98 | 412.73 | 10.7108 | 59.05
5 | 31.5 | 3.41 | 502.02 | 107.8489 | 116.12 | 4.02 | 112.1 | 32.7416 | 509.78 | 399.07 | 675.12 | 810 | 100 | 165.34 | 410.93 | 9.7156 | 65.0985
| 35 | 3.41 | 500.45 | 119.4574 | 120.24 | 1.12 | 119.12 | 34.9012 | 401.84 | 359.01 | 558.54 | 808.95 | 101 | 156.7 | 449.94 | 10.6632 | 59.3137
CST Table | [16 empty] | 0
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 73.2333 | 39.5333 | 73.6 | 70.2 | 75.9 |  |  | 39.9 | 39 | 39.7
2 | 48 | 37.4 | 48.1 | 48.7 | 47.2 | 36.6 |  | 42.2 | 38.2 | 36.6
3 | 46.8333 | 31.05 | 50.2 | 44.7 | 45.6 | 37.4 |  | 31.3 | 31.4 | 30.7 | [9 empty] | Summary - 05 - 03 - 2024 | [7 empty] | Trend over time
4 | 37.7333 | 28.4 | 38.4 | 38.6 | 36.2 | 32.4 |  | 27.1 | 28.8 | 29.3
5 | 28.2333 | 15.8 | 28.3 | 27.3 | 29.1 | 19.8 |  | 22.1 | 12.8 | 12.5
5 | 28.6 | 12 | 27.3 | 29.7 | 28.8 | 19.6 |  | 11.8 | 11.7 | 12.5
Target table
TSS - VSS | [23 empty] | BFP TS | Filtrate TS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%) | [7 empty] | Unit | % | mg TSS/L
1 | 1.1038 | 1.1116 | 10 | 10 | 1.1137 | 1.1225 | 1 | 0.99 | 1.09 | 1.04 | 1.1085 | 1.1138 | 520 | 870 | 695 | [8 empty] | 3 - 3.9 | <= 812
2 | 1.1345 | 1.1268 | 10 | 10 | 1.1422 | 1.1358 | 1 | 0.77 | 0.9 | 0.835 | 1.136 | 1.1286 | 620 | 720 | 670
3 | 1.114 | 1.1224 | 10 | 10 | 1.1231 | 1.1285 | 1 | 0.91 | 0.61 | 0.76 | 1.116 | 1.1233 | 710 | 520 | 615 | [5 empty] | Summary Table
4 | 1.1174 | 1.115 | 10 | 10 | 1.1213 | 1.119 | 1 | 0.39 | 0.4 | 0.395 | 1.1179 | 1.1148 | 340 | 420 | 380 | [8 empty] | batch testing
5 | 1.1218 | 1.1165 | 10 | 10 | 1.1253 | 1.1197 | 1 | 0.35 | 0.32 | 0.335 | 1.1217 | 1.1168 | 360 | 290 | 325 | [6 empty] | unit | Plant | OPD | EPD
6 | 1.1181 | 1.1172 | 10 | 10 | 1.122 | 1.121 | 1 | 0.39 | 0.38 | 0.385 | 1.1181 | 1.1178 | 390 | 320 | 355
Plant Filterate | 1.1103 | 1.1087 | 10 | 10 | 1.1169 | 1.1154 | 1 | 0.66 | 0.67 | 0.665 | 1.111 | 1.1097 | 590 | 570 | 580 | [5 empty] | BFP TS | %TS | 3.7999
. | [20 empty] | Polymer ratio setting | vol/vol | 0.177 | 0.177 | 0.177
[21 empty] | Polymer dose | lb/tonTS | 25.9531 | 32.7416 | 23.6205
TS - VS | [20 empty] | Cake TS | %TS | 28.9719 | 29.7349 | 32.8894
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%) | [6 empty] | Filtrate TSS | mg TSS/L | 580 | 335 | 835
1 | 1.0061 | 1.0124 | 5.2952 | 5.3098 | 2.2718 | 2.3265 | 29.5097 | 30.579 | 30.0443 | 1.4507 | 1.4722 | 15.5065 | 16.0891 | 15.7978
2 | 1.0114 | 1.0056 | 5.2581 | 5.1396 | 2.417 | 2.3566 | 33.0986 | 32.6802 | 32.8894 | 1.5103 | 1.4837 | 17.2439 | 16.9838 | 17.1138
3 | 0.9888 | 1.0072 | 5.2674 | 5.4188 | 2.3317 | 2.306 | 31.3864 | 29.4406 | 30.4135 | 1.4618 | 1.4598 | 16.5148 | 15.616 | 16.0654
4 | 1.004 | 0.9975 | 5.0896 | 5.3244 | 2.2401 | 2.3258 | 30.255 | 30.6987 | 30.4768 | 1.4349 | 1.4602 | 15.8205 | 16.2572 | 16.0389
5 | 1.0014 | 0.9955 | 5.0068 | 5.5062 | 2.2412 | 2.2818 | 30.9532 | 28.5166 | 29.7349 | 1.4295 | 1.44 | 16.212 | 15.2882 | 15.7501
6 | 1.0062 | 0.996 | 5.0685 | 5.1949 | 2.2471 | 2.226 | 30.5467 | 29.2934 | 29.9201 | 1.4378 | 1.4217 | 15.9672 | 15.4825 | 15.7249
Plant Cake | 1.0041 | 0.9928 | 5.3082 | 5.1555 | 2.297 | 2.1544 | 30.0388 | 27.905 | 28.9719 | 1.443 | 1.3901 | 16.0883 | 14.8249 | 15.4566
Sludge | 1.0059 | 0.9798 | 5.0524 | 5.1096 | 1.1594 | 1.137 | 3.7934 | 3.8065 | 3.7999 | 1.0616 | 1.0413 | 1.9357 | 1.8729 | 1.9043
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Note: Based on Sludge | Ave | Diff | Tolerance (%) | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%)
20.0077 | 39.5333 | 73.2333 | 30.0443 | 1040 | 39.5333 | 0 | 20 | 2 | 34.9012 | 29.9201 | 385 | 34.9012 | 29.9201 | 385 |  |  | 73.2333 | 0 | 20 | 2 | 32.7416 | 29.7349 | 335 | 32.7416 | 29.7349 | 335 |  | 30.0443 | 0 | 20 | 2 | 23.6205 | #N/A | #N/A | 812 | #N/A |  | #N/A | 23.6205 | 32.8894 | 835 | yes |  | 25.9531 | 28.9719 | 580 | 3.7999
23.6205 | 37.4 | 48 | 32.8894 | 835 | 38.4667 | 5.3963 | 20 | 2 | [8 empty] | 60.6167 | 34.4561 | 20 | 2 | [7 empty] | 31.4669 | -9.4697 | 20 | 2
27.2586 | 31.05 | 46.8333 | 30.4135 | 760 | 34.225 | 19.2808 | 20 | 2 | [8 empty] | 47.4167 | 22.7385 | 20 | 2 | [7 empty] | 31.6515 | 3.3476 | 20 | 2
29.3805 | 28.4 | 37.7333 | 30.4768 | 395 | 29.725 | 17.0197 | 20 | 2 | [8 empty] | 42.2833 | 20.4218 | 20 | 2 | [7 empty] | 30.4452 | 3.7111 | 20 | 2
32.7416 | 15.8 | 28.2333 | 29.7349 | 335 | 22.1 | 46.8461 | 20 | 2 | [8 empty] | 32.9833 | 33.2282 | 20 | 1 | [7 empty] | 30.1059 | 2.3329 | 20 | 2
34.9012 | 12 | 28.6 | 29.9201 | 385 | 13.9 | 45.7014 | 20 | 1 | [8 empty] | 28.4167 | 13.2895 | 20 | 2 | [7 empty] | 29.8275 | 0.61724 | 20 | 2
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on D32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sub-sample weight
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 readings
Note on D49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on I40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 reading Extra slots are given for outliers
OPD
EPD