## 05_23_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/23/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A5 | Poly Loading (lb) | 546.4368 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.182 | Floc Poly Flow (gpm) | 18.2 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 100 | Poly Floc Flow (mgd) | 0.026208 |  | BFP TS | %TS | 4.9888 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.144 |  | Polymer ratio setting | - | 0.182 | 0.182 | 0.182 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.665 |  | Polymer dose | lb/tonTS | 18 | 9.791 | 9.791 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.9888 | BFP Sludge Loading (dtpd) | 22.0077 |  | Cake TS | %TS | 33.9918 | 30.3568 | 30.3568 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 552 | Plant Polydose (Ib/ton) - method 1 | 24.8293 |  | Filtrate TSS | mg TSS/L | 340 | 860 | 860 | [11 empty] | Analyzer | [13 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 308 | Plant Polydose (Ib/ton) - method 2 | 18
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.9888
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.182
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 18 | 9.791 | 9.791
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 33.9918 | 30.3568 | 30.3568
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 340 | 860 | 860
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~18.00lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =9.79< PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 10 | 4.9888 | 500.5 | 49.9382 | 44.82 | 1 | 43.82 | 8.7749 | 451.27 | 685.96 | 671.61 | 1049.54 | 100 | 220.34 | 363.58 | 12.1565 | 52.0275
2 | 11 | 4.9888 | 500.76 | 54.9605 | 49.92 | 1 | 48.92 | 9.791 | 447.59 | 396.69 | 621.4 | 750.14 | 100 | 173.81 | 353.45 | 13.787 | 45.8747 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 12 | 4.9888 | 500.02 | 59.8683 | 53.72 | 1.12 | 52.6 | 10.5431 | 454.8 | 399.14 | 602.09 | 786.69 | 100 | 147.29 | 387.55 | 16.3912 | 38.5861 | [13 empty] | - EPD < OPD < PD
4 | 13.5 | 4.9888 | 501.08 | 67.4947 | 59.89 | 1.02 | 58.87 | 11.7749 | 406.49 | 685.47 | 562.84 | 1099.77 | 100 | 156.35 | 414.3 | 16.294 | 38.8162 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 15 | 4.9888 | 500.26 | 74.8713 | 67.06 | 0.85 | 66.21 | 13.2648 | 469.97 | 397.29 | 612.18 | 740.28 | 100 | 142.21 | 342.99 | 15.0317 | 42.0759 | [13 empty] | 8.209 | lb/tons
6 | 17 | 4.9888 | 500.51 | 84.8966 | 75.2 | 0.9 | 74.3 | 14.8781 | 473.49 | 690.35 | 620.4 | 1122.87 | 100 | 146.91 | 432.52 | 17.1331 | 36.9152
7 |  | 4.9888 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 171.0667 | #DIV/0! | 189.9 | 193.2 | 130.1
2 | 91.55 | #DIV/0! | 94.9 | 88.2
3 | 76.65 | #DIV/0! | 79.2 | 74.1
4 | 69.15 | #DIV/0! | 73.1 | 65.2
5 | 62.3 | #DIV/0! | 79.6 | 55.2 | 52.1
6 | 57.2 | #DIV/0! | 58.1 | 56.3
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.0997 | 1.1015 | 10 | 10 | 1.1089 | 1.1109 | 1 | 0.92 | 0.94 | 0.93 |  |  | 110890 | 111090 | 111090
2 | 1.1323 | 1.1147 | 10 | 10 | 1.1407 | 1.1235 | 1 | 0.84 | 0.88 | 0.86 |  |  | 114070 | 112350 | 113210
3 | 1.1047 | 1.1048 | 10 | 10 | 1.1265 | 1.1129 | 1 | 0.79 | 0.81 | 0.8 |  |  | 112650 | 111290 | 111970
4 | 1.1057 | 1.1216 | 10 | 10 | 1.111 | 1.1292 | 1 | 0.76 | 0.76 | 0.76 |  |  | 111100 | 112920 | 112920
5 | 1.1186 | 1.122 | 10 | 10 | 1.1249 | 1.1279 | 1 | 0.63 | 0.59 | 0.61 |  |  | 112490 | 112790 | 112790
6 | 1.1034 | 1.1138 | 10 | 10 | 1.11 | 1.12 | 1 | 0.66 | 0.62 | 0.64 |  |  | 111000 | 112000 | 111500
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.0896 | 1.1243 | 10 | 10 | 1.0927 | 1.128 | 1 | 0.31 | 0.37 | 0.34 |  |  | 109270 | 112800 | 112800
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9888 | 0.9967 | 5.3029 | 5.4399 | 2.3699 | 2.4404 | 32.0136 | 32.4923 | 32.253 |  |  | 44.6906 | 44.8611 | 44.7759
2 | 0.9956 | 0.997 | 5.2585 | 5.399 | 2.2924 | 2.3305 | 30.4206 | 30.293 | 30.3568 |  |  | 43.5942 | 43.1654 | 43.3798
3 | 0.9973 | 0.9889 | 5.2271 | 5.273 | 2.269 | 2.2802 | 30.0653 | 30.1417 | 30.1035 |  |  | 43.4084 | 43.2429 | 43.3257
4 | 0.9925 | 0.9846 | 5.2884 | 5.3085 | 2.3564 | 2.359 | 31.7489 | 31.7861 | 31.7675 |  |  | 44.5579 | 44.4382 | 44.498
5 | 0.9905 | 0.9957 | 5.2789 | 5.322 | 2.3222 | 2.3421 | 31.0535 | 31.1213 | 31.0874 |  |  | 43.9902 | 44.0079 | 43.9991
6 | 0.9867 | 0.9858 | 5.2449 | 5.3741 | 2.2856 | 2.3198 | 30.5035 | 30.399 | 30.4513 |  |  | 43.5776 | 43.1663 | 43.3719
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9854 | 0.9703 | 5.3296 | 5.4573 | 2.495 | 2.4615 | 34.7498 | 33.2338 | 33.9918 |  |  | 46.814 | 45.1047 | 45.9594
Sludge | 1.0087 | 0.9938 | 5.2529 | 5.2148 | 1.2178 | 1.207 | 4.9267 | 5.0509 | 4.9888 |  |  | 23.1834 | 23.1457 | 23.1645
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
8.7749 |  | 171.0667 | 32.253 | 930 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 171.0667 |  |  |  | 9.791 | 30.3568 | 860 | 9.791 | 30.3568 | 860 | 0 |  |  | 30.7533 | 2 | 9.791 | 30.3568 | 860 | 1000 | 860 |  | 1 | 9.791 | 30.3568 | 860 | 0 |  | 18 | 33.9918 | 340 | 4.9888 |  |  | 2
9.791 |  | 91.55 | 30.3568 | 860 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 131.3083 | 30.2786 | 10 | 1 | [7 empty] | 1 | 30.3568 | 0.67285 | 3 | [18 empty] | 1
10.5431 |  | 76.65 | 30.1035 | 800 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 84.1 | 8.8585 | 10 | 2 | [7 empty] | 1 | 30.1035 | 30.0804 | 1 | [18 empty] | 1
11.7749 |  | 69.15 | 31.7675 | 760 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 72.9 | 5.144 | 10 | 2 | [7 empty] | 1 | 31.7675 |  | 1 | [18 empty] | 1
13.2648 |  | 62.3 | 31.0874 | 610 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 65.725 | 5.2111 | 10 | 2 | [7 empty] | 1 | 31.0874 |  | 1 | [18 empty] | 1
14.8781 |  | 57.2 | 30.4513 | 640 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 59.75 | 4.2678 | 10 | 2 | [7 empty] | 1 | 30.4513 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 57.2 | 100 | 10 | 2 | [9 empty] | 2.1879 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 05_12_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/12/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A4 | Poly Loading (lb) | 562.0493 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 18.72 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 104 | Poly Floc Flow (mgd) | 0.026957 |  | BFP TS | %TS | 4.3991 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.14976 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.7732 |  | Polymer dose | lb/tonTS | 18 | 11.3361 | 10.416 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.3991 | BFP Sludge Loading (dtpd) | 23.5635 |  | Cake TS | %TS | 31.0342 | 32.8794 | 32.6522 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 526 | Plant Polydose (Ib/ton) - method 1 | 23.8525 |  | Filtrate TSS | mg TSS/L | 375 | 785 | 865 | [11 empty] | Analyzer | [13 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 270 | Plant Polydose (Ib/ton) - method 2 | 18
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.3991
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 18 | 11.3361 | 10.416
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 31.0342 | 32.8794 | 32.6522
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 375 | 785 | 865
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~18.00lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =11.34< PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 10 | 4.3991 | 502.36 | 44.1987 | 43.05 | 0.83 | 42.22 | 9.5523 | 449.2 | 399.07 | 616.42 | 1028.44 | 100 | 167.22 | 629.37 | 19.3315 | 32.7173
2 | 11 | 4.3991 | 500.75 | 48.4628 | 46.91 | 1.02 | 45.89 | 10.416 | 447.56 | 361.75 | 598.73 | 719.74 | 100 | 151.17 | 357.99 | 13.5729 | 46.5981 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 12 | 4.3991 | 502.32 | 53.0342 | 51.19 | 1.09 | 50.1 | 11.3361 | 454.65 | 398.99 | 609.49 | 760.2 | 100 | 154.84 | 361.21 | 13.3317 | 47.4414 | [13 empty] | - EPD < OPD < PD
4 | 13.5 | 4.3991 | 500.35 | 59.4295 | 57.51 | 1 | 56.51 | 12.8368 | 406.41 | 686.13 | 556.02 | 1054.65 | 100 | 149.61 | 368.52 | 13.689 | 46.2031 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 15 | 4.3991 | 500.28 | 66.0236 | 63.13 | 0.86 | 62.27 | 14.1472 | 460.42 | 690.08 | 599.82 | 1062.02 | 100 | 139.4 | 371.94 | 14.3504 | 44.0735 | [13 empty] | 6.6639 | lb/tons
6 | 17 | 4.3991 | 500.87 | 74.9149 | 71.47 | 0.8 | 70.67 | 16.0367 | 463.77 | 363.93 | 588.78 | 782.22 | 100 | 125.01 | 418.29 | 16.7548 | 37.7488
7 |  | 4.3991 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 145.2667 | #DIV/0! | 175.8 | 166.8 | 93.2
2 | 96.8333 | #DIV/0! | 117.3 | 90.1 | 83.1
3 | 70.8 | #DIV/0! | 72.2 | 65.5 | 70.8
4 | 59.2 | #DIV/0! | 64.3 | 59 | 59.2
5 | 49.4667 | #DIV/0! | 57.1 | 47.2 | 44.1
6 | 51.3333 | #DIV/0! | 58 | 48.1 | 47.9
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.096 | 1.0998 | 10 | 10 | 1.105 | 1.1087 | 1 | 0.9 | 0.89 | 0.895 |  |  | 110500 | 110870 | 110870
2 | 1.1013 | 1.1032 | 10 | 10 | 1.1099 | 1.1119 | 1 | 0.86 | 0.87 | 0.865 |  |  | 110990 | 111190 | 111090
3 | 1.128 | 1.1113 | 10 | 10 | 1.136 | 1.119 | 1 | 0.8 | 0.77 | 0.785 |  |  | 113600 | 111900 | 112750
4 | 1.1083 | 1.1103 | 10 | 10 | 1.1161 | 1.1179 | 1 | 0.78 | 0.76 | 0.77 |  |  | 111610 | 111790 | 111790
5 | 1.1091 | 1.1094 | 10 | 10 | 1.1164 | 1.1162 | 1 | 0.73 | 0.68 | 0.705 |  |  | 111640 | 111620 | 111620
6 | 1.1067 | 1.1075 | 10 | 10 | 1.113 | 1.1132 | 1 | 0.63 | 0.57 | 0.6 |  |  | 111300 | 111320 | 111310
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.1067 | 1.1185 | 10 | 10 | 1.1112 | 1.1215 | 1 | 0.45 | 0.3 | 0.375 |  |  | 111120 | 112150 | 112150
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9875 | 0.9912 | 5.1515 | 5.129 | 2.3682 | 2.3549 | 33.158 | 32.9571 | 33.0576 |  |  | 45.9711 | 45.9134 | 45.9423
2 | 0.9866 | 0.9893 | 5.2119 | 5.6208 | 2.3729 | 2.4943 | 32.8095 | 32.4949 | 32.6522 |  |  | 45.5285 | 44.3762 | 44.9524
3 | 0.982 | 0.9848 | 5.158 | 5.3954 | 2.3501 | 2.4402 | 32.761 | 32.9978 | 32.8794 |  |  | 45.5622 | 45.2274 | 45.3948
4 | 0.9819 | 0.9922 | 5.8485 | 5.2298 | 2.5828 | 2.3487 | 32.8957 | 32.011 | 32.4534 |  |  | 44.1618 | 44.9099 | 44.5358
5 | 0.9839 | 0.9906 | 5.4871 | 5.5594 | 2.4261 | 2.4203 | 32.0261 | 31.2927 | 31.6594 |  |  | 44.2146 | 43.5353 | 43.8749
6 | 0.9877 | 0.9807 | 5.3338 | 5.219 | 2.3689 | 2.274 | 31.7802 | 30.5146 | 31.1474 |  |  | 44.413 | 43.5716 | 43.9923
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9924 | 1.0023 | 5.5583 | 5.4494 | 2.3781 | 2.4129 | 30.3489 | 31.7195 | 31.0342 |  |  | 42.7847 | 44.2783 | 43.5315
Sludge | 0.9957 | 0.9928 | 5.1657 | 5.5797 | 1.1884 | 1.1844 | 4.6211 | 4.1771 | 4.3991 |  |  | 23.0056 | 21.2269 | 22.1163
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
9.5523 |  | 145.2667 | 33.0576 | 895 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 145.2667 |  |  |  | 11.3361 | 32.8794 | 785 | 11.3361 | 32.8794 | 785 | 0 |  |  | 32.0349 | 2 | 10.416 | 32.6522 | 865 | 1000 | 865 |  | 1 | 10.416 | 32.6522 | 865 | 0 |  | 18 | 31.0342 | 375 | 4.3991 |  |  | 2
10.416 |  | 96.8333 | 32.6522 | 865 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 121.05 | 20.0055 | 10 | 2 | [9 empty] | 0.77823 | 3 | [18 empty] | 1
11.3361 |  | 70.8 | 32.8794 | 785 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 83.8167 | 15.5299 | 10 | 1 | [7 empty] | 1 | 32.8794 | 31.2567 | 1 | [18 empty] | 1
12.8368 |  | 59.2 | 32.4534 | 770 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 65 | 8.9231 | 10 | 2 | [7 empty] | 1 | 32.4534 |  | 1 | [18 empty] | 1
14.1472 |  | 49.4667 | 31.6594 | 705 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 54.3333 | 8.9571 | 10 | 2 | [7 empty] | 1 | 31.6594 |  | 1 | [18 empty] | 1
16.0367 |  | 51.3333 | 31.1474 | 600 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.4 | -1.8519 | 10 | 2 | [7 empty] | 1 | 31.1474 |  | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 51.3333 | 100 | 10 | 2 | [9 empty] | 2.4293 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 05_05_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/05/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B2 | Poly Loading (lb) | 481.7291 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.184 | Floc Poly Flow (gpm) | 16.0448 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 87.2 | Poly Floc Flow (mgd) | 0.023105 |  | BFP TS | %TS | 4.1826 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12557 |  | Polymer ratio setting | - | 0.184 | 0.184 | 0.184 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.879 |  | Polymer dose | lb/tonTS | 18 | 12.187 | 12.187 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.1826 | BFP Sludge Loading (dtpd) | 20.3113 |  | Cake TS | %TS | 32.1591 | 31.0484 | 31.0484 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 411 | Plant Polydose (Ib/ton) - method 1 | 23.7173 |  | Filtrate TSS | mg TSS/L | 470 | 740 | 740 | [11 empty] | Analyzer | [13 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 194 | Plant Polydose (Ib/ton) - method 2 | 18
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.1826
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.184
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 18 | 12.187 | 12.187
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.1591 | 31.0484 | 31.0484
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 470 | 740 | 740
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~18.00lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =12.19 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 11 | 4.1826 | 501.03 | 46.1038 | 42.42 | 0.87 | 41.55 | 9.9135 | 205.96 | 396.76 | 356.9 | 753.19 | 100 | 150.94 | 356.43 | 12.9829 | 48.7159
2 | 12.5 | 4.1826 | 502.52 | 52.5465 | 47.04 | 0.83 | 46.21 | 10.9926 | 206.08 | 401.21 | 340.71 | 786.51 | 100 | 134.63 | 385.3 | 14.7927 | 42.7556 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 13.5 | 4.1826 | 500.55 | 56.5278 | 51.96 | 0.93 | 51.03 | 12.187 | 449.46 | 361.77 | 591.53 | 738.68 | 100 | 142.07 | 376.91 | 13.8656 | 45.6146 | [13 empty] | - EPD < OPD < PD
4 | 15 | 4.1826 | 503.46 | 63.1738 | 57.87 | 0.91 | 56.96 | 13.5246 | 461.46 | 399.15 | 587.57 | 793.9 | 100 | 126.11 | 394.75 | 15.5193 | 40.7538 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 16.5 | 4.1826 | 500.63 | 69.1005 | 60.49 | 0.96 | 59.53 | 14.2147 | 454.89 | 687.4 | 615.7 | 1061.02 | 100 | 160.81 | 373.62 | 12.4232 | 50.9106 | [13 empty] | 5.813 | lb/tons
6 | 18 | 4.1826 | 500.86 | 75.417 | 68.04 | 1.11 | 66.93 | 15.9744 | 406.9 | 372.09 | 585.13 | 733.47 | 100 | 178.23 | 361.38 | 11.1707 | 56.6191
7 |  | 4.1826 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 117.6333 | #DIV/0! | 134 | 106.1 | 112.8
2 | 92.6333 | #DIV/0! | 99.2 | 96.4 | 82.3
3 | 65.2 | #DIV/0! | 71.2 | 66 | 65.2
4 | 54.2 | #DIV/0! | 64.3 | 58.2 | 54.2
5 | 46.5 | #DIV/0! | 48.8 | 44.2
6 | 43.35 | #DIV/0! | 41.5 | 45.2
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1213 | 1.1232 | 10 | 10 | 1.1317 | 1.1325 | 1 | 1.04 | 0.93 | 0.985 |  |  | 113170 | 113250 | 113250
2 | 1.1267 | 1.1156 | 10 | 10 | 1.1342 | 1.1235 | 1 | 0.75 | 0.79 | 0.77 |  |  | 113420 | 112350 | 112885
3 | 1.121 | 1.1142 | 10 | 10 | 1.1285 | 1.1215 | 1 | 0.75 | 0.73 | 0.74 |  |  | 112850 | 112150 | 112500
4 | 1.121 | 1.0998 | 10 | 10 | 1.1289 | 1.1045 | 1 | 0.79 | 0.47 | 0.63 |  |  | 112890 | 110450 | 110450
5 | 1.1274 | 1.1004 | 10 | 10 | 1.1332 | 1.1082 | 1 | 0.58 | 0.78 | 0.68 |  |  | 113320 | 110820 | 110820
6 | 1.1102 | 1.123 | 10 | 10 | 1.1161 | 1.1272 | 1 | 0.59 | 0.42 | 0.505 |  |  | 111610 | 112720 | 112165
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.121 | 1.1165 | 10 | 10 | 1.1254 | 1.1215 | 1 | 0.44 | 0.5 | 0.47 |  |  | 112540 | 112150 | 112150
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9983 | 1.0003 | 5.4762 | 5.1302 | 2.3045 | 2.2549 | 29.1699 | 30.3785 | 29.7742 |  |  | 42.0821 | 43.9535 | 43.0178
2 | 1.0029 | 0.9993 | 5.8963 | 5.4902 | 2.527 | 2.3727 | 31.146 | 30.5818 | 30.8639 |  |  | 42.8574 | 43.217 | 43.0372
3 | 0.9864 | 0.9862 | 5.5332 | 5.5471 | 2.3977 | 2.4027 | 31.0394 | 31.0575 | 31.0484 |  |  | 43.333 | 43.3145 | 43.3237
4 | 0.9945 | 1.0014 | 5.3025 | 5.1647 | 2.3092 | 2.3059 | 30.5176 | 31.3333 | 30.9255 |  |  | 43.5493 | 44.6473 | 44.0983
5 | 1.024 | 1.0125 | 5.1603 | 5.9672 | 2.3228 | 2.5847 | 31.4 | 31.7315 | 31.5658 |  |  | 45.0129 | 43.3151 | 44.164
6 | 0.9999 | 1.0041 | 5.3904 | 5.2412 | 2.3785 | 2.3548 | 31.3996 | 31.8779 | 31.6388 |  |  | 44.1247 | 44.9286 | 44.5267
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9865 | 0.9912 | 5.2786 | 5.4023 | 2.3875 | 2.3885 | 32.6414 | 31.6769 | 32.1591 |  |  | 45.2298 | 44.2127 | 44.7212
Sludge | 0.9885 | 0.9871 | 5.1657 | 5.5797 | 1.1613 | 1.1813 | 4.1367 | 4.2285 | 4.1826 |  |  | 22.481 | 21.1714 | 21.8262
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
9.9135 |  | 117.6333 | 29.7742 | 985 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 117.6333 |  |  |  | 12.187 | 31.0484 | 740 | 12.187 | 31.0484 | 740 | 0 |  |  | 31.2946 | 2 | 12.187 | 31.0484 | 740 | 1000 | 740 |  | 1 | 12.187 | 31.0484 | 740 | 0 |  | 18 | 32.1591 | 470 | 4.1826 |  |  | 2
10.9926 |  | 92.6333 | 30.8639 | 770 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 105.1333 | 11.8897 | 10 | 2 | [9 empty] | 0.36001 | 2 | [18 empty] | 2
12.187 |  | 65.2 | 31.0484 | 740 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 78.9167 | 17.3812 | 10 | 1 | [7 empty] | 1 | 31.0484 | 30.9346 | 3 | [18 empty] | 1
13.5246 |  | 54.2 | 30.9255 | 630 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 59.7 | 9.2127 | 10 | 2 | [7 empty] | 1 | 30.9255 |  | 2 | [18 empty] | 2
14.2147 |  | 46.5 | 31.5658 | 680 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.35 | 7.6465 | 10 | 2 | [7 empty] | 1 | 31.5658 |  | 1 | [18 empty] | 1
15.9744 |  | 43.35 | 31.6388 | 505 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 44.925 | 3.5058 | 10 | 2 | [7 empty] | 1 | 31.6388 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 43.35 | 100 | 10 | 2 | [9 empty] | 1.1504 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 05_02_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 04/24/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:10 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 480.444 |  | Shampling time | 8:10 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 16.002 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 88.9 | Poly Floc Flow (mgd) | 0.023043 |  | BFP TS | %TS | 3.997 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12802 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.6815 |  | Polymer dose | lb/tonTS | 22.517 | 15.1146 | 13.1669 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.997 | BFP Sludge Loading (dtpd) | 19.653 |  | Cake TS | %TS | 31.7636 | 32.1567 | 31.4638 | [11 empty] | Sampling time |  | 8:10 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 559 | Plant Polydose (Ib/ton) - method 1 | 24.4463 |  | Filtrate TSS | mg TSS/L | 425 | 620 | 710 | [11 empty] | Analyzer | [13 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 308 | Plant Polydose (Ib/ton) - method 2 | 22.517
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.997
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 22.517 | 15.1146 | 13.1669
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 31.7636 | 32.1567 | 31.4638
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 425 | 620 | 710
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~21.61lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =13.17 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 11.5 | 3.997 | 500.11 | 45.9753 | 45.47 | 0.81 | 44.66 | 11.171 | 204.72 | 396.74 | 355.89 | 748.37 | 100 | 151.17 | 351.63 | 12.2043 | 51.8237
2 | 12.5 | 3.997 | 500.77 | 50.0391 | 49.31 | 0.89 | 48.42 | 12.0955 | 206.02 | 401.64 | 365.6 | 754.38 | 100 | 159.58 | 352.74 | 11.7007 | 54.0545 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 13.5 | 3.997 | 501.92 | 54.1664 | 53.52 | 0.69 | 52.83 | 13.1669 | 462.17 | 361.87 | 622.19 | 710.09 | 100 | 160.02 | 348.22 | 11.4859 | 55.0653 | [13 empty] | - EPD < OPD < PD
4 | 15.5 | 3.997 | 500.31 | 61.9915 | 61.27 | 0.82 | 60.45 | 15.1146 | 447.57 | 399.11 | 610.03 | 772.6 | 100 | 162.46 | 373.49 | 11.7644 | 53.7613 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 17 | 3.997 | 501.31 | 68.1266 | 67.75 | 0.29 | 67.46 | 16.8337 | 454.89 | 684.77 | 612.35 | 1054.46 | 100 | 157.46 | 369.69 | 11.7941 | 53.6261 | [13 empty] | 7.4025 | lb/tons
6 | 18 | 3.997 | 500.58 | 72.029 | 71.89 | 0.98 | 70.91 | 17.7204 | 409.45 | 630.91 | 566.86 | 1062.88 | 100 | 157.41 | 431.97 | 13.1087 | 48.2483
7 |  | 3.997 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 111.5333 | #DIV/0! | 132.7 | 102.7 | 99.2
2 | 81.8 | #DIV/0! | 76.8 | 88.2 | 80.4
3 | 64.1 | #DIV/0! | 64.1 | 59.8
4 | 42.4 | #DIV/0! | 42.4 | 38.7
5 | 42.1667 | #DIV/0! | 52.2 | 44.9 | 29.4
6 | 37.5333 | #DIV/0! | 47.2 | 45.4 | 20
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1142 | 1.1268 | 10 | 10 | 1.123 | 1.1349 | 1 | 0.88 | 0.81 | 0.845 |  |  | 112300 | 113490 | 113490
2 | 1.1175 | 1.1235 | 10 | 10 | 1.1252 | 1.1311 | 1 | 0.77 | 0.76 | 0.765 |  |  | 112520 | 113110 | 112815
3 | 1.1268 | 1.1192 | 10 | 10 | 1.1342 | 1.126 | 1 | 0.74 | 0.68 | 0.71 |  |  | 113420 | 112600 | 113010
4 | 1.1125 | 1.1112 | 10 | 10 | 1.1186 | 1.1175 | 1 | 0.61 | 0.63 | 0.62 |  |  | 111860 | 111750 | 111750
5 | 1.1154 | 1.117 | 10 | 10 | 1.1202 | 1.122 | 1 | 0.48 | 0.5 | 0.49 |  |  | 112020 | 112200 | 112200
6 | 1.1188 | 1.1115 | 10 | 10 | 1.1245 | 1.1168 | 1 | 0.57 | 0.53 | 0.55 |  |  | 112450 | 111680 | 112065
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.117 | 1.115 | 10 | 10 | 1.1215 | 1.119 | 1 | 0.45 | 0.4 | 0.425 |  |  | 112150 | 111900 | 111900
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9882 | 0.9977 | 5.1305 | 5.0721 | 2.2066 | 2.2306 | 29.4136 | 30.2597 | 29.8366 |  |  | 43.0095 | 43.9778 | 43.4936
2 | 0.9861 | 1.0027 | 5.6629 | 5.0882 | 2.3974 | 2.275 | 30.1766 | 31.1418 | 30.6592 |  |  | 42.3352 | 44.7113 | 43.5232
3 | 0.9876 | 0.9819 | 5.4949 | 5.1667 | 2.4132 | 2.2917 | 31.6287 | 31.299 | 31.4638 |  |  | 43.9171 | 44.3552 | 44.1361
4 | 0.9968 | 0.9919 | 5.6534 | 5.6117 | 2.4957 | 2.476 | 32.1887 | 32.1248 | 32.1567 |  |  | 44.1451 | 44.1221 | 44.1336
5 | 0.9911 | 0.9979 | 5.1931 | 5.6908 | 2.2891 | 2.439 | 30.8901 | 30.7081 | 30.7991 |  |  | 44.0796 | 42.8586 | 43.4691
6 | 0.9844 | 0.997 | 5.0569 | 5.1063 | 2.3593 | 2.326 | 33.7606 | 32.3413 | 33.0509 |  |  | 46.6551 | 45.5516 | 46.1033
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9934 | 0.9883 | 5.2446 | 5.2321 | 2.3325 | 2.3475 | 31.4993 | 32.0279 | 31.7636 |  |  | 44.4743 | 44.8673 | 44.6708
Sludge | 0.9852 | 0.9932 | 5.3986 | 5.2459 | 1.1621 | 1.1627 | 4.0082 | 3.9857 | 3.997 |  |  | 21.526 | 22.164 | 21.845
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
11.171 |  | 111.5333 | 29.8366 | 845 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 111.5333 |  |  |  | 15.1146 | 32.1567 | 620 | 15.1146 | 32.1567 | 620 | 0 |  |  | 32.0022 | 2 | 13.1669 | 31.4638 | 710 | 1000 | 710 |  | 1 | 13.1669 | 31.4638 | 710 | 0 |  | 22.517 | 31.7636 | 425 | 3.997 |  |  | 2
12.0955 |  | 81.8 | 30.6592 | 765 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 96.6667 | 15.3793 | 10 | 2 | [9 empty] | 1.1339 | 2 | [18 empty] | 2
13.1669 |  | 64.1 | 31.4638 | 710 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 72.95 | 12.1316 | 10 | 2 | [9 empty] | 30.8684 | 3 | [18 empty] | 1
15.1146 |  | 42.4 | 32.1567 | 620 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 53.25 | 20.3756 | 10 | 1 | [7 empty] | 1 | 32.1567 |  | 1 | [18 empty] | 1
16.8337 |  | 42.1667 | 30.7991 | 490 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 42.2833 | 0.27592 | 10 | 2 | [7 empty] | 1 | 30.7991 |  | 2 | [18 empty] | 2
17.7204 |  | 37.5333 | 33.0509 | 550 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 39.85 | 5.8135 | 10 | 2 | [7 empty] | 1 | 33.0509 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 37.5333 | 100 | 10 | 2 | [9 empty] | 3.543 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 03_04_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 02/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 10:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | D3 | Poly Loading (lb) | 466.2607 |  | Shampling time | 10:00 |  |  |  | Parnia | 0 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.184 | Floc Poly Flow (gpm) | 15.5296 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 84.4 | Poly Floc Flow (mgd) | 0.022363 |  | BFP TS | %TS | 4.13 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12154 |  | Polymer ratio setting | - | 0.184 | 0.184 | 0.184 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.36 | Calculated BFP TS (%) | 3.6041 |  | Polymer dose | lb/tonTS | 22.276 | 18.7165 | 12.6895 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.13 | BFP Sludge Loading (dtpd) | 18.266 |  | Cake TS | %TS | 29.839 | 34.4829 | 32.6012 | [11 empty] | Sampling time |  | 10:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 390 | Plant Polydose (Ib/ton) - method 1 | 25.5262 |  | Filtrate TSS | mg TSS/L | 475 | 565 | 795 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 190 | Plant Polydose (Ib/ton) - method 2 | 22.276
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.13
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.184
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 22.276 | 18.7165 | 12.6895
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 29.839 | 34.4829 | 32.6012
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 475 | 565 | 795
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~18.54lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =16.55 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 15 | 4.13 | 501.36 | 62.1185 | 53.67 | 1.12 | 52.55 | 12.6895 | 449.04 | 397.06 | 626.99 | 741.14 | 100 | 177.95 | 344.08 | 10.9662 | 57.6745
2 | 18 | 4.13 | 500.13 | 74.3593 | 64.85 | 1.17 | 63.68 | 15.4149 | 447.38 | 399.03 | 596.01 | 770.08 | 100 | 148.63 | 371.05 | 12.8094 | 49.3755 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 22 | 4.13 | 500.2 | 90.8963 | 78.22 | 0.89 | 77.33 | 18.7165 | 204.57 | 412.6 | 374.61 | 796.35 | 100 | 170.04 | 383.75 | 11.6497 | 54.2911 | [13 empty] | - EPD < OPD < PD
4 | 24 | 4.13 | 501.5 | 99.4173 | 85.65 | 0.96 | 84.69 | 20.4447 | 205.91 | 413.17 | 380.64 | 805.89 | 100 | 174.73 | 392.72 | 11.4747 | 55.1187 | [13 empty] | - We can achieve cost savings by operating at EPD instead of PD.
5 | 26.5 | 4.13 | 504.72 | 110.4781 | 95.52 | 1 | 94.52 | 22.6722 | 454.56 | 396.62 | 622.36 | 798.45 | 100 | 167.8 | 401.83 | 11.8087 | 53.56 | [13 empty] | -2.7622 | lb/tons
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 89.5 | #DIV/0! |  | 89.5
2 | 62.6667 | #DIV/0! | 62.1 |  | 64.2 | 61.7
3 | 35.2 | #DIV/0! | 35.2
4 | 30.8 | #DIV/0! | 30.8
5 | 32.6 | #DIV/0! | 32.6
6
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1165 | 1.1177 | 10 | 10 | 1.1248 | 1.1253 | 1 | 0.83 | 0.76 | 0.795 |  |  | 112480 | 112530 | 112530
2 | 1.0846 | 1.0845 | 10 | 10 | 1.0899 | 1.0914 | 1 | 0.53 | 0.69 | 0.61 |  |  | 108990 | 109140 | 109140
3 | 1.1037 | 1.1162 | 10 | 10 | 1.1097 | 1.1215 | 1 | 0.6 | 0.53 | 0.565 |  |  | 110970 | 112150 | 111560
4 | 1.1252 | 1.1177 | 10 | 10 | 1.1303 | 1.1229 | 1 | 0.51 | 0.52 | 0.515 |  |  | 113030 | 112290 | 112660
5 | 1.1232 | 1.1021 | 10 | 10 | 1.1277 | 1.1067 | 1 | 0.45 | 0.46 | 0.455 |  |  | 112770 | 110670 | 110670
6
Plant Filterate | 1.1178 | 1.1135 | 10 | 10 | 1.1224 | 1.1184 | 1 | 0.46 | 0.49 | 0.475 |  |  | 112240 | 111840 | 111840
.
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9876 | 0.9897 | 6.542 | 5.2767 | 2.7922 | 2.3921 | 32.4896 | 32.7129 | 32.6012 |  |  | 42.6811 | 45.3333 | 44.0072
2 | 0.9884 | 0.9876 | 6.3932 | 6.542 | 2.4698 | 2.4246 | 27.409 | 25.8714 | 26.6402 |  |  | 38.6317 | 37.0621 | 37.8469
3 | 0.9915 | 1.0074 | 5.3647 | 5.8934 | 2.5118 | 2.6785 | 34.764 | 34.2018 | 34.4829 |  |  | 46.8209 | 45.4491 | 46.135
4 | 0.9802 | 0.9961 | 6.329 | 6.1651 | 2.6806 | 2.6696 | 31.7903 | 32.3757 | 32.083 |  |  | 40.4259 | 45.2981 | 42.862
5 | 0.9983 | 1.0064 | 6.6309 | 5.7382 | 2.7988 | 2.4505 | 31.9657 | 30.519 | 31.2424 |  |  | 42.2084 | 39.7479 | 40.9782
Plant Cake | 0.9763 | 1.0172 | 5.6324 | 5.584 | 2.3646 | 2.3809 | 29.8168 | 29.8612 | 29.839 |  |  | 41.9821 | 42.6379 | 42.31
Sludge | 0.9878 | 0.998 | 6.035 | 6.3177 | 1.1863 | 1.2283 | 3.9329 | 4.3292 | 4.131 |  |  | 19.657 | 19.4422 | 19.5496
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | 0.9876 |  | 6.542 |  | 2.4246 |  | 25.8714 | #DIV/0! | #DIV/0! |  |  | 37.0621 | #DIV/0! | #DIV/0!
3 | 0.9915 |  | 5.3647 |  | 2.5118 |  | 34.764 | #DIV/0! | #DIV/0! |  |  | 46.8209 | #DIV/0! | #DIV/0!
4 | 0.9894 |  | 5.8174 |  | 3.0084 |  | 41.8186 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 0.9983 |  | 6.6309 |  | 2.7988 |  | 31.9657 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6
Plant Cake | 0.9763 |  | 5.6324 |  | 2.3646 |  | 29.8168 | #DIV/0! | #DIV/0! |  |  | 41.9821 | #DIV/0! | #DIV/0!
Sludge | 0.9835 |  | 5.9908 |  | 1.2069 |  | 4.4615 | #DIV/0! | #DIV/0! |  |  | 20.1459 | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.6895 | #DIV/0! | 89.5 | 32.6012 | 795 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 89.5 |  |  |  | 18.7165 | 34.4829 | 565 | 18.7165 | 34.4829 | 565 | 0 |  |  | 32.6028 | 3 | 12.6895 | 32.6012 | 795 | 1000 | 795 |  | 1 | 12.6895 | 32.6012 | 795 | 0 |  | 22.276 | 29.839 | 475 | 4.131 |  |  | 1
15.4149 | #DIV/0! | 62.6667 | 26.6402 | 610 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 76.0833 | 17.6342 | 10 | 2 | [9 empty] | 1.6816 | 2 | [18 empty] | 2
18.7165 | #DIV/0! | 35.2 | 34.4829 | 565 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 48.9333 | 28.0654 | 10 | 1 | [7 empty] | 1 | 34.4829 | 30.9211 | 1 | [18 empty] | 1
20.4447 | #DIV/0! | 30.8 | 32.083 | 515 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 33 | 6.6667 | 10 | 2 | [7 empty] | 1 | 32.083 |  | 1 | [18 empty] | 1
22.6722 | #DIV/0! | 32.6 | 31.2424 | 455 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 31.7 | -2.8391 | 10 | 2 | [7 empty] | 1 | 31.2424 |  | 1 | [18 empty] | 1
[31 empty] | 2 | [18 empty] | 2
[30 empty] | 5.1579 | 2 | [18 empty] | 2
[31 empty] | 2 | [18 empty] | 2
`
Haydee's calculations
is EPD cake TS < than OPD cake TS or higher?
[28 empty] | 32.6028 |  | 30.9211
1.6816
[27 empty] | error% | 5.1579 | (<10% to have valid data for EPD determination)
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 03_07_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/07/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 485.5962 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.184 | Floc Poly Flow (gpm) | 16.1736 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 87.9 | Poly Floc Flow (mgd) | 0.02329 |  | BFP TS | %TS | 3.89 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12658 |  | Polymer ratio setting | - | 0.184 | 0.184 | 0.184 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.5 | Calculated BFP TS (%) | 3.7255 |  | Polymer dose | lb/tonTS | 23.6504 | 18.8844 | 18.8844 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.89 | BFP Sludge Loading (dtpd) | 19.6642 |  | Cake TS | %TS | 30.7567 | 31.7 | 31.7 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 443 | Plant Polydose (Ib/ton) - method 1 | 24.6944 |  | Filtrate TSS | mg TSS/L | 480 | 590 | 590 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 211 | Plant Polydose (Ib/ton) - method 2 | 23.6504
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.89
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.184
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 23.6504 | 18.8844 | 18.8844
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 30.7567 | 31.7 | 31.7
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 480 | 590 | 590
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~18.54lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =21.57 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 15 | 3.89 | 500.45 | 58.4025 | 62.11 | 0.95 | 61.16 | 15.7082 | 204.72 | 686.16 | 374.36 | 1051.62 | 100 | 169.64 | 365.46 | 10.9341 | 57.8441
2 | 18 | 3.89 | 500.27 | 70.0578 | 74.6 | 1.1 | 73.5 | 18.8844 | 214.53 | 396.54 | 357.63 | 793.07 | 100 | 143.1 | 396.53 | 12.7901 | 49.4503 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 20.5 | 3.89 | 500.9 | 79.8885 | 85.27 | 1.21 | 84.06 | 21.5704 | 467.28 | 397.15 | 613.69 | 805.85 | 100 | 146.41 | 408.7 | 12.6294 | 50.0794 | [13 empty] | - EPD < OPD < PD
4 | 22.5 | 3.89 | 500.24 | 87.567 | 94.29 | 1.35 | 92.94 | 23.8806 | 450.96 | 684.51 | 604.96 | 1099.07 | 100 | 154 | 414.56 | 12.1115 | 52.2209 | [13 empty] | - We can achieve cost savings by operating at EPD instead of PD.
5 | 25 | 3.89 | 500.86 | 97.4172 | 104.33 | 1.27 | 103.06 | 26.4481 | 452.81 | 399.31 | 561.71 | 822.92 | 100 | 108.9 | 423.61 | 15.7756 | 40.0918 | [13 empty] | 4.766 | lb/tons
0
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 102.7 | #DIV/0! | 102.7
2 | 58.2 | #DIV/0! | 58.2 | 52.4 | 47.8
3 | 50.05 | #DIV/0! | 55.5 | 44.6
4 | 51.4 | #DIV/0! | 51.4
5 | 51.9 | #DIV/0! | 51.9 | 49.7 | 48.9
6
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1282 | 1.1271 | 10 | 10 | 1.1361 | 1.1352 | 1 | 0.79 | 0.81 | 0.8 |  |  | 113610 | 113520 | 113520
2 | 1.1223 | 1.1069 | 10 | 10 | 1.1281 | 1.1129 | 1 | 0.58 | 0.6 | 0.59 |  |  | 112810 | 111290 | 111290
3 | 1.1047 | 1.1174 | 10 | 10 | 1.11 | 1.1226 | 1 | 0.53 | 0.52 | 0.525 |  |  | 111000 | 112260 | 111630
4 | 1.1185 | 1.099 | 10 | 10 | 1.1227 | 1.1033 | 1 | 0.42 | 0.43 | 0.425 |  |  | 112270 | 110330 | 111300
5 | 1.1064 | 1.1036 | 10 | 10 | 1.1102 | 1.1074 | 1 | 0.38 | 0.38 | 0.38 |  |  | 111020 | 110740 | 110740
6
Plant Filterate | 1.1188 | 1.0853 | 10 | 10 | 1.1236 | 1.0901 | 1 | 0.48 | 0.48 | 0.48 |  |  | 112360 | 109010 | 109010
.
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 1 | 0.9964 | 5.3609 | 5.3664 | 2.369 | 2.3859 | 31.3926 | 31.7963 | 31.5945 |  |  | 44.1903 | 44.46 | 44.3252
2 | 1.0071 | 1.0006 | 5.1549 | 5.1329 | 2.3236 | 2.3089 | 31.7397 | 31.6603 | 31.7 |  |  | 45.0756 | 44.9824 | 45.029
3 | 0.9915 | 0.9897 | 5.2801 | 5.2716 | 2.2606 | 2.2352 | 29.5924 | 29.0876 | 29.34 |  |  | 42.8136 | 42.4008 | 42.6072
4 | 1.0011 | 0.9978 | 5.2631 | 5.3671 | 2.2925 | 2.313 | 30.3003 | 30.1009 | 30.2006 |  |  | 44.3278 | 43.8766 | 44.1022
5 | 1.0021 | 0.9992 | 5.1717 | 5.3471 | 2.3444 | 2.4044 | 32.1925 | 32.3191 | 32.2558 |  |  | #DIV/0! | 44.7989 | #DIV/0!
Plant Cake | 0.9966 | 0.997 | 5.2052 | 5.2481 | 2.2836 | 2.312 | 30.5802 | 30.9332 | 30.7567 |  |  | 43.8715 | 44.054 | 43.9628
Sludge | 0.9931 | 0.9985 | 5.3306 | 5.3135 | 1.1661 | 1.1617 | 3.9885 | 3.7822 | 3.8853 |  |  | 21.8756 | 21.8632 | 21.8694
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | #REF!
4 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | #REF!
5 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
6
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
15.7082 | #DIV/0! | 102.7 | 31.5945 | 800 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 102.7 |  |  |  | 18.8844 | 31.7 | 590 | 18.8844 | 31.7 | 590 | 0 |  |  | 30.8741 | 2 | 18.8844 | 31.7 | 590 | 1000 | 590 |  | 1 | 18.8844 | 31.7 | 590 | 0 |  | 23.6504 | 30.7567 | 480 | 3.8853 |  |  | 2
18.8844 | #DIV/0! | 58.2 | 31.7 | 590 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 80.45 | 27.6569 | 10 | 1 | [7 empty] | 1 | 31.7 | 1.3414 | 3 | [18 empty] | 1
21.5704 | #DIV/0! | 50.05 | 29.34 | 525 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 54.125 | 7.5289 | 10 | 2 | [7 empty] | 1 | 29.34 | 29.5327 | 2 | [18 empty] | 2
23.8806 | #DIV/0! | 51.4 | 30.2006 | 425 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.725 | -1.3307 | 10 | 2 | [7 empty] | 1 | 30.2006 |  | 1 | [18 empty] | 1
26.4481 | #DIV/0! | 51.9 | 32.2558 | 380 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 51.65 | -0.48403 | 10 | 2 | [7 empty] | 1 | 32.2558 |  | 1 | [18 empty] | 1
[31 empty] | 2 | [18 empty] | 2
[30 empty] | 4.3448 | 2 | [18 empty] | 2
[31 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 03_13_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/13/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A3 | Poly Loading (lb) | 450.7923 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.184 | Floc Poly Flow (gpm) | 15.0144 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 81.6 | Poly Floc Flow (mgd) | 0.021621 |  | BFP TS | %TS | 3.55 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.1175 |  | Polymer ratio setting | - | 0.184 | 0.184 | 0.184 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.11 | Calculated BFP TS (%) | 3.307 |  | Polymer dose | lb/tonTS | 25.9155 | 22.9169 | 15.7774 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.55 | BFP Sludge Loading (dtpd) | 16.2041 |  | Cake TS | %TS | 34.5214 | 32.0244 | 31.7179 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 354 | Plant Polydose (Ib/ton) - method 1 | 27.8196 |  | Filtrate TSS | mg TSS/L | 380 | 605 | 690 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 193 | Plant Polydose (Ib/ton) - method 2 | 25.9155
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.55
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.184
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 25.9155 | 22.9169 | 15.7774
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 34.5214 | 32.0244 | 31.7179
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 380 | 605 | 690
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~25.92lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =22.91< PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 12 | 3.55 | 500.2 | 42.617 | 47.23 | 1.11 | 46.12 | 12.9864 | 457.6 | 686.17 | 605.22 | 1063.12 | 100 | 147.62 | 376.95 | 11.55 | 54.7594
2 | 14.5 | 3.55 | 501.34 | 51.6129 | 56.91 | 0.75 | 56.16 | 15.7774 | 204.55 | 362.01 | 340.88 | 753.18 | 100 | 136.33 | 391.17 | 12.3523 | 51.2029 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 18 | 3.55 | 500.37 | 63.9473 | 70.59 | 0.89 | 69.7 | 19.6193 | 205.87 | 685.4 | 345.88 | 1097.96 | 100 | 140.01 | 412.56 | 12.2976 | 51.4306 | [13 empty] | - EPD < OPD < PD
4 | 21 | 3.55 | 500.03 | 74.5545 | 82.15 | 0.79 | 81.36 | 22.9169 | 449.13 | 399.11 | 600.88 | 804.11 | 100 | 151.75 | 405 | 11.2018 | 56.4616 | [13 empty] | - We can achieve cost savings by operating at EPD instead of PD.
5 | 23.6 | 3.55 | 500.18 | 83.8101 | 92.2 | 1.18 | 91.02 | 25.6302 | 447.4 | 684.66 | 604.46 | 1095.53 | 100 | 157.06 | 410.87 | 10.8605 | 58.2361 | [13 empty] | 10.1381 | lb/tons
|  | 3.89 |  |  |  |  | 0 | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 103.5333 | #DIV/0! | 110.1 | 102 | 98.5
2 | 77.7 | #DIV/0! | 77.7 | 62.9
3 | 54.6 | #DIV/0! | 58.2 | 51
4 | 22.65 | #DIV/0! | 23.2 | 22.1
5 | 23.7 | #DIV/0! | 23.9 | 23.5
6
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1112 | 1.1025 | 10 | 10 | 1.1214 | 1.1124 | 1 | 1.02 | 0.99 | 1.005 |  |  | 112140 | 111240 | 111240
2 | 1.1108 | 1.1288 | 10 | 10 | 1.1192 | 1.1342 | 1 | 0.84 | 0.54 | 0.69 |  |  | 111920 | 113420 | 113420
3 | 1.1287 | 1.1151 | 10 | 10 | 1.1347 | 1.1207 | 1 | 0.6 | 0.56 | 0.58 |  |  | 113470 | 112070 | 112770
4 | 1.103 | 1.1007 | 10 | 10 | 1.1093 | 1.1065 | 1 | 0.63 | 0.58 | 0.605 |  |  | 110930 | 110650 | 110790
5 | 1.1029 | 1.1028 | 10 | 10 | 1.1067 | 1.1068 | 1 | 0.38 | 0.4 | 0.39 |  |  | 110670 | 110680 | 110680
6
Plant Filterate | 1.1286 | 1.1336 | 10 | 10 | 1.1329 | 1.1369 | 1 | 0.43 | 0.33 | 0.38 |  |  | 113290 | 113690 | 113690
.
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9854 | 0.9987 | 5.4478 | 5.4025 | 2.2914 | 2.2854 | 29.2668 | 29.2179 | 29.2424 |  |  | 42.061 | 42.3026 | 42.1818
2 | 0.995 | 1.0028 | 5.6335 | 5.5148 | 2.4499 | 2.4498 | 31.3657 | 32.07 | 31.7179 |  |  | 43.4881 | 44.4223 | 43.9552
3 | 1.0006 | 0.9921 | 5.2687 | 5.3083 | 2.3544 | 2.314 | 31.719 | 30.6265 | 31.1728 |  |  | 44.6865 | 43.5921 | 44.1393
4 | 0.989 | 0.994 | 5.5764 | 5.4474 | 2.4628 | 2.4156 | 32.1271 | 31.9217 | 32.0244 |  |  | 46.383 | 45.5061 | 45.9446
5 | 0.9893 | 0.9994 | 5.3097 | 5.2456 | 2.3625 | 2.3347 | 31.7841 | 31.4469 | 31.6155 |  |  | #DIV/0! | 42.859 | #DIV/0!
Plant Cake | 0.9929 | 0.9967 | 5.3476 | 5.4778 | 2.4943 | 2.5456 | 34.4777 | 34.5652 | 34.5214 |  |  | 46.6434 | 46.4712 | 46.5573
Sludge | 0.9776 | 1.0057 | 5.5808 | 5.6896 | 1.1351 | 1.178 | 3.4215 | 3.6786 | 3.55 |  |  | 20.3394 | 20.7044 | 20.5219
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | #REF!
4 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | #REF!
5 |  |  | 10 | 10 |  |  | 1 | #REF! | 0 | #REF! |  |  | #REF! | 0 | 0
6
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.9864 | #DIV/0! | 103.5333 | 29.2424 | 1005 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 103.5333 |  |  |  | 22.9169 | 32.0244 | 605 | 22.9169 | 32.0244 | 605 | 0 |  |  | 31.82 | 2 | 15.7774 | 31.7179 | 690 | 1000 | 690 |  | 1 | 15.7774 | 31.7179 | 690 | 0 |  | 25.9155 | 34.5214 | 380 | 3.55 |  |  | 2
15.7774 | #DIV/0! | 77.7 | 31.7179 | 690 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 90.6167 | 14.2542 | 10 | 2 | [9 empty] | 0.28913 | 3 | [18 empty] | 1
19.6193 | #DIV/0! | 54.6 | 31.1728 | 580 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 66.15 | 17.4603 | 10 | 2 | [9 empty] | 31.5308 | 2 | [18 empty] | 2
22.9169 | #DIV/0! | 22.65 | 32.0244 | 605 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 38.625 | 41.3592 | 10 | 1 | [7 empty] | 1 | 32.0244 |  | 1 | [18 empty] | 1
25.6302 | #DIV/0! | 23.7 | 31.6155 | 390 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 23.175 | -2.2654 | 10 | 2 | [7 empty] | 1 | 31.6155 |  | 1 | [18 empty] | 1
[31 empty] | 2 | [18 empty] | 2
[30 empty] | 0.90863 | 2 | [18 empty] | 2
[31 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_29_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 04/24/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 10:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A4 | Poly Loading (lb) | 545.8363 |  | Shampling time | 10:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 18.18 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 101 | Poly Floc Flow (mgd) | 0.026179 |  | BFP TS | %TS | 3.8969 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.14544 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.548 |  | Polymer dose | lb/tonTS | 23.0954 | 15.8232 | 13.8295 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.8969 | BFP Sludge Loading (dtpd) | 21.5183 |  | Cake TS | %TS | 30.6466 | 32.1638 | 32.6139 | [11 empty] | Sampling time |  | 10:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 471 | Plant Polydose (Ib/ton) - method 1 | 25.3662 |  | Filtrate TSS | mg TSS/L | 420 | 535 | 735 | [11 empty] | Analyzer | [13 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 287 | Plant Polydose (Ib/ton) - method 2 | 23.0954
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.8969
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 23.0954 | 15.8232 | 13.8295
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 30.6466 | 32.1638 | 32.6139
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 420 | 535 | 735
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~21.61lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =13.37 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 11.5 | 3.8969 | 501.95 | 44.9888 | 46.58 | 0.8 | 45.78 | 11.7022 | 407.24 | 399.05 | 564.02 | 761.78 | 100 | 156.78 | 362.73 | 11.8335 | 53.4475
2 | 12.5 | 3.8969 | 501.77 | 48.8834 | 50.76 | 0.65 | 50.11 | 12.8137 | 396.64 | 449.34 | 605.08 | 744.27 | 100 | 208.44 | 294.93 | 8.5562 | 73.9194 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 13.5 | 3.8969 | 504.53 | 53.0844 | 55.28 | 0.9 | 54.38 | 13.8295 | 361.75 | 447.51 | 612.02 | 712.51 | 100 | 250.27 | 265 | 7.2425 | 87.328 | [13 empty] | - EPD < OPD < PD
4 | 15.5 | 3.8969 | 500.72 | 60.4885 | 62.46 | 0.71 | 61.75 | 15.8232 | 409.67 | 204.73 | 360.13 | 790.3 | 100 | -49.54 | 585.57 | -37.5358 | -16.8499 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 17 | 3.8969 | 500.26 | 66.2813 | 68.3 | 0.65 | 67.65 | 17.351 | 408.2 | 205.95 | 365.74 | 796.28 | 100 | -42.46 | 590.33 | -44.2925 | -14.2794 | [13 empty] | 7.2722 | lb/tons
6 | 18 | 3.8969 | 502.26 | 70.4608 | 72.7 | 0.72 | 71.98 | 18.3881 | 401.14 | 460.78 | 619.26 | 786.84 | 100 | 218.12 | 326.06 | 8.5035 | 74.3777
7 |  | 3.8969 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 127.85 | #DIV/0! | 127.2 | 128.5
2 | 81.7333 | #DIV/0! | 75.6 | 68.7 | 100.9
3 | 57.2 | #DIV/0! | 57.2 | 92.2 | 86.8
4 | 44 | #DIV/0! | 44 | 58.7
5 | 41.85 | #DIV/0! | 42.2 | 41.5
6 | 57.6667 | #DIV/0! | 56.4 | 61.3 | 55.3
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.125 | 1.1222 | 10 | 10 | 1.1336 | 1.1301 | 1 | 0.86 | 0.79 | 0.825 |  |  | 113360 | 113010 | 113010
2 | 1.1108 | 1.1297 | 10 | 10 | 1.1181 | 1.1373 | 1 | 0.73 | 0.76 | 0.745 |  |  | 111810 | 113730 | 112770
3 | 1.1137 | 1.1191 | 10 | 10 | 1.1211 | 1.1264 | 1 | 0.74 | 0.73 | 0.735 |  |  | 112110 | 112640 | 112375
4 | 1.1288 | 1.1171 | 10 | 10 | 1.1343 | 1.1223 | 1 | 0.55 | 0.52 | 0.535 |  |  | 113430 | 112230 | 112230
5 | 1.102 | 1.1132 | 10 | 10 | 1.1066 | 1.1178 | 1 | 0.46 | 0.46 | 0.46 |  |  | 110660 | 111780 | 111780
6 | 1.1162 | 1.1151 | 10 | 10 | 1.1211 | 1.1203 | 1 | 0.49 | 0.52 | 0.505 |  |  | 112110 | 112030 | 112070
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.1105 | 1.1271 | 10 | 10 | 1.1145 | 1.1315 | 1 | 0.4 | 0.44 | 0.42 |  |  | 111450 | 113150 | 113150
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9972 | 0.9904 | 5.4448 | 5.4175 | 2.2542 | 2.3506 | 28.2624 | 30.7244 | 29.4934 |  |  | 41.401 | 43.389 | 42.395
2 | 0.9999 | 0.9891 | 6.4722 | 6.8596 | 2.5992 | 2.7805 | 29.2254 | 30.5153 | 29.8703 |  |  | 40.1595 | 40.5344 | 40.3469
3 | 0.9824 | 1.0055 | 5.5315 | 5.612 | 2.4657 | 2.5082 | 32.6064 | 32.6213 | 32.6139 |  |  | 44.5756 | 44.6935 | 44.6346
4 | 0.9771 | 0.9904 | 5.5739 | 5.7204 | 2.4438 | 2.5239 | 31.907 | 32.4207 | 32.1638 |  |  | 43.8436 | 44.121 | 43.9823
5 | 0.9801 | 0.9975 | 5.1178 | 5.9131 | 2.32 | 2.5948 | 32.3827 | 32.4945 | 32.4386 |  |  | 45.332 | 43.8822 | 44.6071
6 | 1.0054 | 1.0017 | 6.223 | 5.2984 | 2.7084 | 2.3942 | 32.6395 | 32.4086 | 32.5241 |  |  | 43.5224 | 45.1872 | 44.3548
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 1.0037 | 1.0063 | 5.7319 | 5.1264 | 2.4597 | 2.2629 | 30.794 | 30.4993 | 30.6466 |  |  | 42.9125 | 44.1421 | 43.5273
Sludge | 0.9932 | 0.9807 | 10.0473 | 10.2853 | 1.3466 | 1.3427 | 3.9032 | 3.8905 | 3.8969 | 1.1183 | 1.1094 | 2.2723 | 2.2683 | 2.2703
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1175 |  | 10 | 10 | 1.1256 |  | 1 | 0.81 | 0 | 0.405 |  |  | 112560 | 0 | 0
2 | 1.1102 |  | 10 | 10 | 1.1175 |  | 1 | 0.73 | 0 | 0.365 |  |  | 111750 | 0 | 0
3 | 1.1137 |  | 10 | 10 | 1.1211 |  | 1 | 0.74 | 0 | 0.37 |  |  | 112110 | 0 | 56055
4 | 1.1171 |  | 10 | 10 | 1.1223 |  | 1 | 0.52 | 0 | 0.26 |  |  | 112230 | 0 | 56115
5 | 1.1132 |  | 10 | 10 | 1.1178 |  | 1 | 0.46 | 0 | 0.23 |  |  | 111780 | 0 | 0
6 | 1.1211 |  | 10 | 10 | 1.1262 |  | 1 | 0.51 | 0 | 0.255 |  |  | 112620
Plant Filterate | 1.1249 |  | 10 | 10 | 1.1293 |  | 1 | 0.44 | 0 | 0.22 |  |  | 112930 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9879 |  | 5.6399 |  | 2.3931 |  | 30.2064 | #DIV/0! | #DIV/0! |  |  | 42.4316 | #DIV/0! | #DIV/0!
2 | 0.9826 |  | 5.7219 |  | 2.3132 |  | 28.0759 | #DIV/0! | #DIV/0! |  |  | 40.4271 | #DIV/0! | #DIV/0!
3 | 0.977 |  | 5.3655 |  | 2.4528 |  | 33.6288 | #DIV/0! | #DIV/0! |  |  | 45.7143 | #DIV/0! | #DIV/0!
4 | 0.9904 |  | 5.7204 |  | 2.5239 |  | 32.4207 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 1.0074 |  | 6.3277 |  | 2.6911 |  | 31.6467 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6 | 1.0016 |  | 6.0394 |  | 2.6071 |  | 31.8691 | #REF! | #REF!
Plant Cake | 0.9898 |  | 5.921 |  | 2.4943 |  | 30.5098 | #DIV/0! | #DIV/0! |  |  | 42.1263 | #DIV/0! | #DIV/0!
Sludge | 0.9968 |  | 10.956 |  | 1.3886 |  | 3.9341 | #DIV/0! | #DIV/0! | 1.137 |  | 2.2965 | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
11.7022 |  | 127.85 | 29.4934 | 825 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 127.85 |  |  |  | 15.8232 | 32.1638 | 535 | 15.8232 | 32.1638 | 535 | 0 |  |  | 32.3755 | 2 | 13.8295 | 32.6139 | 735 | 1000 | 735 |  | 1 | 13.8295 | 32.6139 | 735 | 0 |  | 23.0954 | 30.6466 | 420 | 3.8969 |  |  | 2
12.8137 |  | 81.7333 | 29.8703 | 745 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 104.7917 | 22.004 | 10 | 2 | [9 empty] | 0.18822 | 2 | [18 empty] | 2
13.8295 |  | 57.2 | 32.6139 | 735 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 69.4667 | 17.6583 | 10 | 2 | [9 empty] | 32.1873 | 3 | [18 empty] | 1
15.8232 |  | 44 | 32.1638 | 535 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.6 | 13.0435 | 10 | 1 | [7 empty] | 1 | 32.1638 |  | 2 | [18 empty] | 2
17.351 |  | 41.85 | 32.4386 | 460 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 42.925 | 2.5044 | 10 | 2 | [7 empty] | 1 | 32.4386 |  | 1 | [18 empty] | 1
18.3881 |  | 57.6667 | 32.5241 | 505 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 49.7583 | -15.8935 | 10 | 2 | [7 empty] | 1 | 32.5241 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 57.6667 | 100 | 10 | 2 | [9 empty] | 0.58135 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_25_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 04/24/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:45 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 418.8108 |  | Shampling time | 8:45 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.172 | Floc Poly Flow (gpm) | 13.9492 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 81.1 | Poly Floc Flow (mgd) | 0.020087 |  | BFP TS | %TS | 3.98 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11678 |  | Polymer ratio setting | - | 0.172 | 0.172 | 0.172 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.6684 |  | Polymer dose | lb/tonTS | 21.608 | 13.3663 | 12.3776 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.98 | BFP Sludge Loading (dtpd) | 17.8647 |  | Cake TS | %TS | 32.1397 | 30.2564 | 31.2709 | [11 empty] | Sampling time |  | 8:45 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 451 | Plant Polydose (Ib/ton) - method 1 | 23.4435 |  | Filtrate TSS | mg TSS/L | 425 | 860 | 915 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 251 | Plant Polydose (Ib/ton) - method 2 | 21.608
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.98
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.172
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 21.608 | 13.3663 | 12.3776
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.1397 | 30.2564 | 31.2709
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 425 | 860 | 915
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~21.61lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =13.37 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 11.5 | 3.98 | 501.53 | 45.91 | 46.54 | 1.03 | 45.51 | 11.3998 | 204.7 | 397.55 | 360.83 | 746.06 | 100 | 156.13 | 348.51 | 11.7939 | 53.6272
2 | 12.5 | 3.98 | 501.9 | 49.939 | 50.4 | 0.95 | 49.45 | 12.3776 | 205.99 | 402.55 | 352.43 | 775.14 | 100 | 146.44 | 372.59 | 12.8412 | 49.2534 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 13.5 | 3.98 | 500.96 | 53.8331 | 54.21 | 0.91 | 53.3 | 13.3663 | 449.19 | 361.5 | 601.04 | 728.51 | 100 | 151.85 | 367.01 | 12.2916 | 51.4557 | [13 empty] | - EPD < OPD < PD
4 | 15.5 | 3.98 | 500.5 | 61.7517 | 62.2 | 0.98 | 61.22 | 15.3665 | 447.51 | 399.08 | 595.86 | 790.16 | 100 | 148.35 | 391.08 | 12.8948 | 49.0486 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 17 | 3.98 | 500.6 | 67.7412 | 68.12 | 1.05 | 67.07 | 16.8316 | 454.75 | 685.43 | 595.05 | 1087.16 | 100 | 140.3 | 401.73 | 13.5595 | 46.6442 | [13 empty] | 8.2417 | lb/tons
6 | 18 | 3.98 | 500.83 | 71.7589 | 72.95 | 1.03 | 71.92 | 18.0404 | 406.42 | 684.85 | 561.47 | 1086.3 | 100 | 155.05 | 401.45 | 12.4911 | 50.6337
7 |  | 3.98 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 124.7 | #DIV/0! | 141.2 | 108.6 | 124.3
2 | 80.5667 | #DIV/0! | 84.2 | 67.2 | 90.3
3 | 58.5 | #DIV/0! | 37.6 | 52.7 | 85.2
4 | 60.5 | #DIV/0! | 60.5 | 68.96
5 | 54.2 | #DIV/0! | 58.2 | 54.2
6 | 50.9 | #DIV/0! | 45.3 | 50.9
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1191 | 1.0997 | 10 | 10 | 1.1286 | 1.1105 | 1 | 0.95 | 1.08 | 1.015 |  |  | 112860 | 111050 | 111050
2 | 1.0989 | 1.0986 | 10 | 10 | 1.1086 | 1.1072 | 1 | 0.97 | 0.86 | 0.915 |  |  | 110860 | 110720 | 110790
3 | 1.1049 | 1.0958 | 10 | 10 | 1.1132 | 1.1047 | 1 | 0.83 | 0.89 | 0.86 |  |  | 111320 | 110470 | 110895
4 | 1.1035 | 1.1126 | 10 | 10 | 1.1124 | 1.1202 | 1 | 0.89 | 0.76 | 0.825 |  |  | 111240 | 112020 | 112020
5 | 1.0906 | 1.1049 | 10 | 10 | 1.0982 | 1.1112 | 1 | 0.76 | 0.63 | 0.695 |  |  | 109820 | 111120 | 111120
6 | 1.1062 | 1.1055 | 10 | 10 | 1.1114 | 1.1116 | 1 | 0.52 | 0.61 | 0.565 |  |  | 111140 | 111160 | 111150
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.1212 | 1.1136 | 10 | 10 | 1.1255 | 1.1178 | 1 | 0.43 | 0.42 | 0.425 |  |  | 112550 | 111780 | 111780
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9996 | 0.996 | 5.0772 | 5.1965 | 2.1875 | 2.209 | 29.1323 | 28.8775 | 29.0049 |  |  | 43.0848 | 42.5094 | 42.7971
2 | 0.9978 | 0.9952 | 5.301 | 5.0324 | 2.2995 | 2.2989 | 30.2496 | 32.2922 | 31.2709 |  |  | 43.3786 | 45.682 | 44.5303
3 | 0.9968 | 1.0003 | 5.088 | 5.0207 | 2.2245 | 2.2267 | 30.0083 | 30.5044 | 30.2564 |  |  | 43.7205 | 44.3504 | 44.0355
4 | 0.9982 | 0.9945 | 5.5879 | 5.1353 | 2.3807 | 2.297 | 30.1218 | 31.4553 | 30.7885 |  |  | 42.6046 | 44.7296 | 43.6671
5 | 0.9824 | 0.9964 | 5.0245 | 5.1423 | 2.2478 | 2.2741 | 31.3055 | 30.8184 | 31.062 |  |  | 44.7368 | 44.2234 | 44.4801
6 | 0.9857 | 0.9887 | 5.1227 | 5.1685 | 2.2784 | 2.2982 | 31.2473 | 31.3293 | 31.2883 |  |  | 44.4765 | 44.4655 | 44.471
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9976 | 1.0013 | 5.1314 | 5.0734 | 2.323 | 2.3132 | 32.0625 | 32.2168 | 32.1397 |  |  | 45.2703 | 45.5947 | 45.4325
Sludge | 1.0053 | 1.009 | 5.1049 | 5.137 | 1.1613 | 1.1523 | 3.8052 | 3.4714 | 3.6383 |  |  | 22.7487 | 22.4314 | 22.5901
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
11.3998 |  | 124.7 | 29.0049 | 1015 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 124.7 |  |  |  | 13.3663 | 30.2564 | 860 | 13.3663 | 30.2564 | 860 | 0 |  |  | 30.8488 | 2 | 12.3776 | 31.2709 | 915 | 1000 | 915 |  | 1 | 12.3776 | 31.2709 | 915 | 0 |  | 21.608 | 32.1397 | 425 | 3.6383 |  |  | 2
12.3776 |  | 80.5667 | 31.2709 | 915 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 102.6333 | 21.5005 | 10 | 2 | [9 empty] | 0.44466 | 3 | [18 empty] | 1
13.3663 |  | 58.5 | 30.2564 | 860 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 69.5333 | 15.8677 | 10 | 1 | [7 empty] | 1 | 30.2564 | 30.4041 | 2 | [18 empty] | 2
15.3665 |  | 60.5 | 30.7885 | 825 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 59.5 | -1.6807 | 10 | 2 | [7 empty] | 1 | 30.7885 |  | 1 | [18 empty] | 1
16.8316 |  | 54.2 | 31.062 | 695 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 57.35 | 5.4926 | 10 | 2 | [7 empty] | 1 | 31.062 |  | 1 | [18 empty] | 1
18.0404 |  | 50.9 | 31.2883 | 565 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 52.55 | 3.1399 | 10 | 2 | [7 empty] | 1 | 31.2883 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.9 | 100 | 10 | 2 | [9 empty] | 1.4414 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [22 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_18_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 413.4305 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.162 | Floc Poly Flow (gpm) | 13.77 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 85 | Poly Floc Flow (mgd) | 0.019829 |  | BFP TS | %TS | 3.98 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.1224 |  | Polymer ratio setting | - | 0.162 | 0.162 | 0.162 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.5581 |  | Polymer dose | lb/tonTS | 20.3518 | 14.0093 | 14.0093 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.98 | BFP Sludge Loading (dtpd) | 18.1608 |  | Cake TS | %TS | 31.5957 | 30.1658 | 30.1658 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 501 | Plant Polydose (Ib/ton) - method 1 | 22.765 |  | Filtrate TSS | mg TSS/L | 550 | 785 | 785 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 303 | Plant Polydose (Ib/ton) - method 2 | 20.3518
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.98
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.162
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 20.3518 | 14.0093 | 14.0093
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 31.5957 | 30.1658 | 30.1658
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 550 | 785 | 785
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~20.35b/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =15.05 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 13 | 3.98 | 500.7 | 51.8124 | 52.29 | 0.7 | 51.59 | 12.9442 | 204.71 | 381.82 | 368.76 | 716.87 | 100 | 164.05 | 335.05 | 10.9775 | 57.6151
2 | 14 | 3.98 | 502.18 | 55.9629 | 56.88 | 0.88 | 56 | 14.0093 | 205.69 | 398.97 | 361.61 | 769.71 | 100 | 155.92 | 370.74 | 12.0947 | 52.2931 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 15 | 3.98 | 500.59 | 59.7704 | 60.57 | 0.6 | 59.97 | 15.0501 | 454.9 | 684.65 | 601.76 | 1040.96 | 100 | 146.86 | 356.31 | 12.1774 | 51.9382 | [13 empty] | - EPD =OPD < PD
4 | 16.5 | 3.98 | 501.88 | 65.9169 | 65.84 | 1.05 | 64.79 | 16.2179 | 453.69 | 685.46 | 635.44 | 1047.22 | 100 | 181.75 | 361.76 | 10.5411 | 60.0006 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 18.5 | 3.98 | 500.24 | 73.6653 | 74.07 | 0.7 | 73.37 | 18.4258 | 408.44 | 401.52 | 572.84 | 791.58 | 100 | 164.4 | 390.06 | 11.7061 | 54.0292 | [13 empty] | 6.3425 | lb/tons
6 | 20.5 | 3.98 | 503.34 | 82.135 | 82.19 | 0.7 | 81.49 | 20.339 | 460.18 | 685.81 | 630.21 | 1054.21 | 100 | 170.03 | 368.4 | 10.8472 | 58.3073
7 |  | 3.98 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 110.1 | #DIV/0! | 125 | 110.1
2 | 89.85 | #DIV/0! | 91.5 | 88.2
3 | 74.45 | #DIV/0! | 80.5 | 68.4
4 | 55.45 | #DIV/0! | 58.8 | 52.1
5 | 39.15 | #DIV/0! | 30.1 | 40.1 | 38.2
6 | 46.2 | #DIV/0! | 47.4 | 46.2
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1145 | 1.1254 | 10 | 10 | 1.1235 | 1.1342 | 1 | 0.9 | 0.88 | 0.89 |  |  | 112350 | 113420 | 113420
2 | 1.1167 | 1.1243 | 10 | 10 | 1.1249 | 1.1318 | 1 | 0.82 | 0.75 | 0.785 |  |  | 112490 | 113180 | 112835
3 | 1.1283 | 1.1189 | 10 | 10 | 1.1356 | 1.1264 | 1 | 0.73 | 0.75 | 0.74 |  |  | 113560 | 112640 | 113100
4 | 1.111 | 1.1103 | 10 | 10 | 1.1172 | 1.1168 | 1 | 0.62 | 0.65 | 0.635 |  |  | 111720 | 111680 | 111680
5 | 1.1142 | 1.1166 | 10 | 10 | 1.1192 | 1.1225 | 1 | 0.5 | 0.59 | 0.545 |  |  | 111920 | 112250 | 112250
6 | 1.1197 | 1.1108 | 10 | 10 | 1.1237 | 1.1157 | 1 | 0.4 | 0.49 | 0.445 |  |  | 112370 | 111570 | 111970
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.1123 | 1.1158 | 10 | 10 | 1.1175 | 1.1216 | 1 | 0.52 | 0.58 | 0.55 |  |  | 111750 | 112160 | 112160
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9964 | 0.9965 | 5.0441 | 5.0505 | 2.1521 | 2.1354 | 28.552 | 28.0932 | 28.3226 |  |  | 42.6657 | 42.281 | 42.4733
2 | 0.9954 | 0.993 | 5.124 | 5.1483 | 2.2567 | 2.2305 | 30.5503 | 29.7812 | 30.1658 |  |  | 44.0418 | 43.325 | 43.6834
3 | 0.9875 | 0.9974 | 5.1057 | 5.1623 | 2.2766 | 2.3074 | 31.3025 | 31.4533 | 31.3779 |  |  | 44.5894 | 44.6971 | 44.6433
4 | 0.9912 | 0.9972 | 5.1441 | 5.1541 | 2.3006 | 2.3078 | 31.5298 | 31.5283 | 31.529 |  |  | 44.7231 | 44.776 | 44.7495
5 | 0.9985 | 0.9952 | 5.2045 | 5.4432 | 2.3089 | 2.3748 | 31.1555 | 31.0162 | 31.0858 |  |  | 44.3635 | 43.6287 | 43.9961
6 | 1.0021 | 0.9996 | 5.5044 | 5.1855 | 2.4087 | 2.3312 | 31.2418 | 31.8116 | 31.5267 |  |  | 43.7595 | 44.9561 | 44.3578
7 | 0.9924 | 1.0102 | 5.4025 | 5.5115 | 2.4012 | 2.4167 | 31.9449 | 31.2465 | 31.5957 |  |  | 44.4461 | 43.8483 | 44.1472
Plant Cake | 1.0021 | 1.0024 | 5.1669 | 5.148 | 2.3155 | 2.3287 | 31.5357 | 31.993 | 31.7643 |  |  | 44.8141 | 45.235 | 45.0246
Sludge | 1.002 | 0.9867 | 5.2524 | 5.1024 | 1.1675 | 1.1544 | 3.8938 | 4.0746 | 3.9842 |  |  | 22.2279 | 22.6246 | 22.4263
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1177 |  | 10 | 10 | 1.1306 |  | 1 | 1.29 | 0 | 0.645 |  |  | 113060 | 0 | 0
2 | 1.1114 |  | 10 | 10 | 1.117 |  | 1 | 0.56 | 0 | 0.28 |  |  | 111700 | 0 | 0
3 | 1.1109 |  | 10 | 10 | 1.1177 |  | 1 | 0.68 | 0 | 0.34 |  |  | 111770 | 0 | 55885
4 | 1.1047 |  | 10 | 10 | 1.1119 |  | 1 | 0.72 | 0 | 0.36 |  |  | 111190 | 0 | 55595
5 | 1.1167 |  | 10 | 10 | 1.1218 |  | 1 | 0.51 | 0 | 0.255 |  |  | 112180 | 0 | 0
6 | 1.1123 |  | 10 | 10 | 1.1175 |  | 1 | 0.52 | 0 | 0.26 |  |  | 111750
Plant Filterate | 1.117 |  | 10 | 10 | 1.1221 |  | 1 | 0.51 | 0 | 0.255 |  |  | 112210 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9999 |  | 5.1907 |  |  |  | -23.8594 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
2 | 0.9876 |  | 6.2707 |  |  |  | -18.6936 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
3 | 0.9891 |  | 6.511 |  |  |  | -17.9123 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
4 | 1.0059 |  | 6.1162 |  |  |  | -19.6838 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 0.9844 |  | 5.6181 |  |  |  | -21.2444 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6 | 0.9915 |  | 5.388 |  |  |  | -22.552 | #REF! | #REF!
Plant Cake | 1.0046 |  | 5.8274 |  |  |  | -20.8302 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.9442 |  | 110.1 | 28.3226 | 890 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 110.1 |  |  |  | 14.0093 | 30.1658 | 785 | 14.0093 | 30.1658 | 785 | 0 |  |  | 31.1371 | 2 | 14.0093 | 30.1658 | 785 | 1000 | 785 |  | 1 | 14.0093 | 30.1658 | 785 | 0 |  | 20.3518 | 31.5957 | 550 | 3.9842 |  |  | 2
14.0093 |  | 89.85 | 30.1658 | 785 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 99.975 | 10.1275 | 10 | 1 | [7 empty] | 1 | 30.1658 | 0.57216 | 2 | [18 empty] | 2
15.0501 |  | 74.45 | 31.3779 | 740 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 82.15 | 9.3731 | 10 | 2 | [7 empty] | 1 | 31.3779 | 30.5649 | 3 | [18 empty] | 1
16.2179 |  | 55.45 | 31.529 | 635 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 64.95 | 14.6266 | 10 | 2 | [7 empty] | 1 | 31.529 |  | 1 | [18 empty] | 1
18.4258 |  | 39.15 | 31.0858 | 545 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.3 | 17.2304 | 10 | 1 | [7 empty] | 1 | 31.0858 |  | 1 | [18 empty] | 1
20.339 |  | 46.2 | 31.5267 | 445 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 42.675 | -8.2601 | 10 | 2 | [7 empty] | 1 | 31.5267 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 46.2 | 100 | 10 | #DIV/0! | [9 empty] | 1.8376 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [10 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_15_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 9:45 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B5 | Poly Loading (lb) | 358.8168 |  | Shampling time | 9:45 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.19 | Floc Poly Flow (gpm) | 11.951 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 62.9 | Poly Floc Flow (mgd) | 0.017209 |  | BFP TS | %TS | 3.95 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.090576 |  | Polymer ratio setting | - | 0.19 | 0.19 | 0.19 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.6254 |  | Polymer dose | lb/tonTS | 24.0506 | 14.27 | 12.0579 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.95 | BFP Sludge Loading (dtpd) | 13.6932 |  | Cake TS | %TS | 32.6107 | 36.6187 | 36.947 | [11 empty] | Sampling time |  | 9:45 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 320 | Plant Polydose (Ib/ton) - method 1 | 26.204 |  | Filtrate TSS | mg TSS/L | 560 | 495 | 730 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 184 | Plant Polydose (Ib/ton) - method 2 | 24.0506
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.95
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.19
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 24.0506 | 14.27 | 12.0579
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.6107 | 36.6187 | 36.947
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 560 | 495 | 730
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~22.78lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =15.47 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 10 | 3.95 | 500.41 | 39.5324 | 40.54 | 0.61 | 39.93 | 10.1006 | 461.85 | 361.73 | 595.01 | 725.81 | 100 | 133.16 | 364.08 | 13.6599 | 46.3013
2 | 11 | 3.95 | 501.16 | 43.5508 | 44.29 | 0.61 | 43.68 | 11.0326 | 454.5 | 401.07 | 596.67 | 771.64 | 100 | 142.17 | 370.57 | 13.1037 | 48.2667 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 12 | 3.95 | 500.33 | 47.4313 | 48.41 | 0.75 | 47.66 | 12.0579 | 454.78 | 396.67 | 601.15 | 760.04 | 100 | 146.37 | 363.37 | 12.5597 | 50.3575 | [13 empty] | - EPD < OPD < PD
4 | 13 | 3.95 | 500.63 | 51.4147 | 52.23 | 0.78 | 51.45 | 13.0089 | 406.64 | 399.1 | 552.55 | 772.45 | 100 | 145.91 | 373.35 | 12.7471 | 49.6169 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 14 | 3.95 | 500.03 | 55.3033 | 57.1 | 0.73 | 56.37 | 14.27 | 204.77 | 323.91 | 352.39 | 695.32 | 100 | 147.62 | 371.41 | 12.4811 | 50.6744 | [13 empty] | 9.7806 | lb/tons
6 | 16 | 3.95 | 500.09 | 63.2114 | 64.25 | 0.98 | 63.27 | 16.0148 | 206.04 | 326.18 | 360.5 | 713.92 | 100 | 154.46 | 387.74 | 12.3084 | 51.3853
7 |  | 3.95 |  | 0 |  |  | 0 | #DIV/0! |  |  |  |  | 100 | 0 | 0 | #DIV/0! | #DIV/0!
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 132.1 | #DIV/0! |  | 134.7 | 129.5
2 | 120.95 | #DIV/0! | 108.5 | 133.4
3 | 95.7333 | #DIV/0! | 76.4 | 93.1 | 117.7
4 | 61.93 | #DIV/0! | 64.9 | 58.96
5 | 48.6 | #DIV/0! | 41.9 | 48.6
6 | 48.2 | #DIV/0! | 42.3 | 48.2
7 | #DIV/0! | #DIV/0!
| #DIV/0! | #DIV/0!
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1207 | 1.1225 | 10 | 10 | 1.1323 | 1.1348 | 1 | 1.16 | 1.23 | 1.195 |  |  | 113230 | 113480 | 113480
2 | 1.1275 | 1.1148 | 10 | 10 | 1.134 | 1.1214 | 1 | 0.65 | 0.66 | 0.655 |  |  | 113400 | 112140 | 112770
3 | 1.1217 | 1.1153 | 10 | 10 | 1.1292 | 1.1224 | 1 | 0.75 | 0.71 | 0.73 |  |  | 112920 | 112240 | 112580
4 | 1.1114 | 1.1005 | 10 | 10 | 1.1188 | 1.1078 | 1 | 0.74 | 0.73 | 0.735 |  |  | 111880 | 110780 | 110780
5 | 1.1287 | 1.0995 | 10 | 10 | 1.1336 | 1.1045 | 1 | 0.49 | 0.5 | 0.495 |  |  | 113360 | 110450 | 110450
6 | 1.1094 | 1.1224 | 10 | 10 | 1.1151 | 1.1268 | 1 | 0.57 | 0.44 | 0.505 |  |  | 111510 | 112680 | 112095
7 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
Plant Filterate | 1.1215 | 1.1155 | 10 | 10 | 1.1269 | 1.1213 | 1 | 0.54 | 0.58 | 0.56 |  |  | 112690 | 112130 | 112130
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9978 | 1.0004 | 5.475 | 5.125 | 2.509 | 2.3861 | 33.7532 | 33.596 | 33.6746 |  |  | 45.8265 | 46.558 | 46.1923
2 | 1.0037 | 0.9996 | 5.9976 | 5.4885 | 2.7035 | 2.5272 | 34.0375 | 34.0306 | 34.0341 |  |  | 45.0764 | 46.0454 | 45.5609
3 | 0.9859 | 0.9835 | 5.5224 | 6.5885 | 2.7791 | 2.9097 | 39.5283 | 34.3657 | 36.947 |  |  | 50.3241 | 44.1633 | 47.2437
4 | 0.9946 | 1.0011 | 6.3066 | 5.1532 | 2.7162 | 2.3412 | 32.4096 | 32.2752 | 32.3424 |  |  | 43.0692 | 45.432 | 44.2506
5 | 1.0138 | 1.0154 | 5.1564 | 5.981 | 2.5061 | 2.8633 | 36.0233 | 37.214 | 36.6187 |  |  | 48.6017 | 47.8733 | 48.2375
6 | 1.0001 | 1.0032 | 5.387 | 6.234 | 2.5986 | 2.8866 | 36.438 | 36.006 | 36.222 |  |  | 48.2384 | 46.3041 | 47.2712
7 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 0.9894 | 0.9982 | 5.1376 | 6.6057 | 2.3561 | 2.808 | 32.9468 | 32.2746 | 32.6107 |  |  | 45.8599 | 42.5087 | 44.1843
Sludge | 0.9762 | 0.9912 | 5.9027 | 5.1027 | 1.1663 | 1.149 | 3.8587 | 3.838 | 3.8484 |  |  | 19.7588 | 22.5175 | 21.1381
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1177 |  | 10 | 10 | 1.1306 |  | 1 | 1.29 | 0 | 0.645 |  |  | 113060 | 0 | 0
2 | 1.1114 |  | 10 | 10 | 1.117 |  | 1 | 0.56 | 0 | 0.28 |  |  | 111700 | 0 | 0
3 | 1.1109 |  | 10 | 10 | 1.1177 |  | 1 | 0.68 | 0 | 0.34 |  |  | 111770 | 0 | 55885
4 | 1.1047 |  | 10 | 10 | 1.1119 |  | 1 | 0.72 | 0 | 0.36 |  |  | 111190 | 0 | 55595
5 | 1.1167 |  | 10 | 10 | 1.1218 |  | 1 | 0.51 | 0 | 0.255 |  |  | 112180 | 0 | 0
6 | 1.1123 |  | 10 | 10 | 1.1175 |  | 1 | 0.52 | 0 | 0.26 |  |  | 111750
Plant Filterate | 1.117 |  | 10 | 10 | 1.1221 |  | 1 | 0.51 | 0 | 0.255 |  |  | 112210 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9999 |  | 5.1907 |  |  |  | -23.8594 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
2 | 0.9876 |  | 6.2707 |  |  |  | -18.6936 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
3 | 0.9891 |  | 6.511 |  |  |  | -17.9123 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
4 | 1.0059 |  | 6.1162 |  |  |  | -19.6838 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 0.9844 |  | 5.6181 |  |  |  | -21.2444 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6 | 0.9915 |  | 5.388 |  |  |  | -22.552 | #REF! | #REF!
Plant Cake | 1.0046 |  | 5.8274 |  |  |  | -20.8302 | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
10.1006 |  | 132.1 | 33.6746 | 1195 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 132.1 |  |  |  | 14.27 | 36.6187 | 495 | 14.27 | 36.6187 | 495 | 0 |  |  | 36.4203 | 2 | 12.0579 | 36.947 | 730 | 1000 | 730 |  | 1 | 12.0579 | 36.947 | 730 | 0 |  | 24.0506 | 32.6107 | 560 | 3.8484 |  |  | 2
11.0326 |  | 120.95 | 34.0341 | 655 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 126.525 | 4.4062 | 10 | 2 | [9 empty] | 0.28048 | 2 | [18 empty] | 2
12.0579 |  | 95.7333 | 36.947 | 730 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 108.3417 | 11.6376 | 10 | 2 | [9 empty] | 36.1398 | 3 | [18 empty] | 1
13.0089 |  | 61.93 | 32.3424 | 735 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 78.8317 | 21.4402 | 10 | 2 | [10 empty] | 2 | [18 empty] | 2
14.27 |  | 48.6 | 36.6187 | 495 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 55.265 | 12.0601 | 10 | 1 | [7 empty] | 1 | 36.6187 |  | 1 | [18 empty] | 1
16.0148 |  | 48.2 | 36.222 | 505 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 48.4 | 0.41322 | 10 | 2 | [7 empty] | 1 | 36.222 |  | 1 | [18 empty] | 1
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 48.2 | 100 | 10 | #DIV/0! | [9 empty] | 0.77011 | 2 | [18 empty] | 2
[5 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [10 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_11_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 572.8579 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 19.08 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 106 | Poly Floc Flow (mgd) | 0.027475 |  | BFP TS | %TS | 3.95 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.15264 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.6673 |  | Polymer dose | lb/tonTS | 22.7848 | 15.475 | 15.475 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.95 | BFP Sludge Loading (dtpd) | 23.3426 |  | Cake TS | %TS | 32.3649 | 31.1381 | 31.1381 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 535 | Plant Polydose (Ib/ton) - method 1 | 24.5413 |  | Filtrate TSS | mg TSS/L | 350 | 495 | 495 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 298 | Plant Polydose (Ib/ton) - method 2 | 22.7848
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.95
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 22.7848 | 15.475 | 15.475
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.3649 | 31.1381 | 31.1381
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 350 | 495 | 495
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~22.78lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =15.47 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 13 | 3.95 | 501.73 | 51.5277 | 54.27 | 0.85 | 53.42 | 13.4774 | 204.8 | 399.05 | 346.84 | 777.73 | 100 | 142.04 | 378.68 | 13.0873 | 48.3271
2 | 14 | 4.15 | 500.58 | 58.1674 | 58.54 | 0.86 | 57.68 | 13.8827 | 205.93 | 685.36 | 344.35 | 1063.97 | 100 | 138.42 | 378.61 | 13.8996 | 45.5029 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 15.5 | 4.15 | 501.86 | 64.5643 | 65.39 | 0.93 | 64.46 | 15.475 | 449.16 | 400.23 | 606.4 | 783.53 | 100 | 157.24 | 383.3 | 12.6425 | 50.0274 | [13 empty] | - EPD < OPD < PD
4 | 17 | 4.15 | 501.55 | 70.7687 | 71.16 | 0.85 | 70.31 | 16.8898 | 447.44 | 668.5 | 602.94 | 1075.05 | 100 | 155.5 | 406.55 | 13.1558 | 48.0756 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 19 | 4.15 | 501.19 | 79.0376 | 79.37 | 1.03 | 78.34 | 18.8323 | 454.6 | 687.66 | 612.93 | 1074.47 | 100 | 158.33 | 386.81 | 12.3572 | 51.1826 | [13 empty] | 7.3098 | lb/tons
6 | 20 | 4.15 | 500.65 | 83.1079 | 84.05 | 1.1 | 82.95 | 19.962 | 406.34 | 901.36 | 568.68 | 1343.3 | 100 | 162.34 | 441.94 | 13.2519 | 47.7267
7 | 21.5 | 4.15 | 500.23 | 89.266 | 89.65 | 1.11 | 88.54 | 21.3251 | 461.91 | 405.12 | 607.85 | 821.42 | 100 | 145.94 | 416.3 | 13.5837 | 46.561
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 108.8 | #DIV/0! | 114.7 | 102.9
2 | 82.7 |  | 82.7 | 79.1 | 73.4
3 | 52.4 |  | 52.4 | 58.9
4 | 48.5 |  | 48.5 | 42.3
5 | 34.1 |  | 41 | 35.8 | 34.1
6 | 37.8 |  | 38.8 | 37.8 | 42.9
7 | 38.1 |  | 38.1 | 37.5
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1473 | 1.1266 | 10 | 10 | 1.1551 | 1.1355 | 1 | 0.78 | 0.89 | 0.835 |  |  | 115510 | 113550 | 113550
2 | 1.1176 | 1.1238 | 10 | 10 | 1.1234 | 1.1299 | 1 | 0.58 | 0.61 | 0.595 |  |  | 112340 | 112990 | 112665
3 | 1.1223 | 1.1177 | 10 | 10 | 1.1272 | 1.1227 | 1 | 0.49 | 0.5 | 0.495 |  |  | 112720 | 112270 | 112495
4 | 1.1107 | 1.1062 | 10 | 10 | 1.1154 | 1.111 | 1 | 0.47 | 0.48 | 0.475 |  |  | 111540 | 111100 | 111100
5 | 1.1151 | 1.1154 | 10 | 10 | 1.1192 | 1.1192 | 1 | 0.41 | 0.38 | 0.395 |  |  | 111920 | 111920 | 111920
6 | 1.1255 | 1.1086 | 10 | 10 | 1.1291 | 1.1122 | 1 | 0.36 | 0.36 | 0.36 |  |  | 112910 | 111220 | 112065
7 | 1.1007 | 1.1123 | 10 | 10 | 1.1044 | 1.1156 | 1 | 0.37 | 0.33 | 0.35 |  |  | 110440 | 111560 | 111560
Plant Filterate | 1.1115 | 1.1149 | 10 | 10 | 1.1137 | 1.1174 | 1 | 0.22 | 0.25 | 0.235 |  |  | 111370 | 111740 | 111740
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9925 | 0.9955 | 5.0456 | 5.0505 | 2.14 | 2.1164 | 28.3117 | 27.6424 | 27.977 |  |  | 42.4132 | 41.9048 | 42.159
2 | 0.9843 | 0.9934 | 5.1731 | 5.1483 | 2.1534 | 2.1107 | 27.9101 | 26.8911 | 27.4006 |  |  | 41.6269 | 40.998 | 41.3124
3 | 1.0022 | 1.0054 | 5.107 | 5.1623 | 2.2756 | 2.3046 | 31.0222 | 31.2541 | 31.1381 |  |  | 44.5584 | 44.6429 | 44.6007
4 | 0.9989 | 0.9967 | 5.1441 | 5.1541 | 2.2926 | 2.3056 | 31.2096 | 31.4836 | 31.3466 |  |  | 44.5676 | 44.7333 | 44.6504
5 | 0.998 | 0.9947 | 5.2037 | 5.4432 | 2.2839 | 2.3084 | 30.5752 | 29.5313 | 30.0532 |  |  | 43.8899 | 42.4089 | 43.1494
6 | 1.0092 | 1.0099 | 5.5314 | 5.1855 | 2.3365 | 2.492 | 29.3508 | 35.4943 | 32.4225 |  |  | 42.2407 | 48.0571 | 45.1489
7 | 0.9991 | 1.0133 | 5.3165 | 5.5115 | 2.4815 | 2.3805 | 34.3355 | 30.3944 | 32.3649 |  |  | 46.6754 | 43.1915 | 44.9335
Plant Cake | 1.0051 | 1.017 | 5.1638 | 5.148 | 2.316 | 2.3179 | 31.5219 | 31.4912 | 31.5065 |  |  | 44.8507 | 45.0253 | 44.938
Sludge | 1.0026 | 0.9884 | 5.2536 | 5.0828 | 1.1682 | 1.1521 | 3.8956 | 3.9981 | 3.9468 |  |  | 22.2362 | 22.6666 | 22.4514
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
13.4774 |  | 108.8 | 27.977 | 835 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 108.8 |  |  |  | 15.475 | 31.1381 | 495 | 15.475 | 31.1381 | 495 | 0 |  |  | 31.4651 | 2 | 15.475 | 31.1381 | 495 | 1000 | 495 |  | 1 | 15.475 | 31.1381 | 495 | 0 |  | 22.7848 | 32.3649 | 350 | 3.9468 |  |  | 2
13.8827 |  | 82.7 | 27.4006 | 595 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 95.75 | 13.6292 | 10 | 2 | [9 empty] | 0.97988 | 2 | [18 empty] | 2
15.475 |  | 52.4 | 31.1381 | 495 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 67.55 | 22.4278 | 10 | 1 | [7 empty] | 1 | 31.1381 | 30.4852 | 3 | [18 empty] | 1
16.8898 |  | 48.5 | 31.3466 | 475 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.45 | 3.8652 | 10 | 2 | [7 empty] | 1 | 31.3466 |  | 1 | [18 empty] | 1
18.8323 |  | 34.1 | 30.0532 | 395 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 41.3 | 17.4334 | 10 | 1 | [7 empty] | 1 | 30.0532 |  | 2 | [18 empty] | 2
19.962 |  | 37.8 | 32.4225 | 360 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 35.95 | -5.146 | 10 | 2 | [7 empty] | 1 | 32.4225 |  | 1 | [18 empty] | 1
21.3251 |  | 38.1 | 32.3649 | 350 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 37.95 | -0.39526 | 10 | 2 | [7 empty] | 1 | 32.3649 | 3.1142 | 1 | [18 empty] | 1
0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 19.05 | 100 | 10 | 2 | [10 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_04_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 484.7615 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.179 | Floc Poly Flow (gpm) | 16.1458 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 90.2 | Poly Floc Flow (mgd) | 0.02325 |  | BFP TS | %TS | 4.11 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12989 |  | Polymer ratio setting | - | 0.179 | 0.179 | 0.179 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.7608 |  | Polymer dose | lb/tonTS | 21.7762 | 13.8968 | 13.8968 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.11 | BFP Sludge Loading (dtpd) | 20.3695 |  | Cake TS | %TS | 33.415 | 31.6794 | 31.6794 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 355 | Plant Polydose (Ib/ton) - method 1 | 23.7984 |  | Filtrate TSS | mg TSS/L | 350 | 710 | 710 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 184 | Plant Polydose (Ib/ton) - method 2 | 21.7762
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.11
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.179
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 21.7762 | 13.8968 | 13.8968
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 33.415 | 31.6794 | 31.6794
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 350 | 710 | 710
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~22.15lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =18.95 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 13 | 4.11 | 501.59 | 53.5999 | 54.58 | 1.14 | 53.44 | 12.9612 | 212.62 | 361.75 | 353.43 | 752.8 | 100 | 140.81 | 391.05 | 14.0294 | 45.082
2 | 14 | 4.11 | 501.7 | 57.7356 | 58.11 | 0.8 | 57.31 | 13.8968 | 206.08 | 399.14 | 350.5 | 778.82 | 100 | 144.42 | 379.68 | 13.3861 | 47.2485 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 15.5 | 4.11 | 501.85 | 63.9407 | 64.7 | 0.87 | 63.83 | 15.4732 | 472.23 | 369.27 | 610.53 | 767.46 | 100 | 138.3 | 398.19 | 14.1444 | 44.7154 | [13 empty] | - EPD < OPD < PD
4 | 17 | 4.11 | 500.47 | 69.9357 | 70.92 | 0.9 | 70.02 | 17.0205 | 461.74 | 684.65 | 612.49 | 1074.65 | 100 | 150.75 | 390 | 12.9334 | 48.9024 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 19 | 4.11 | 500.27 | 78.1321 | 78.8 | 1.06 | 77.74 | 18.9046 | 448.3 | 938.63 | 603.35 | 1327.6 | 100 | 155.05 | 388.97 | 12.4811 | 50.6743 | [13 empty] | 7.8794 | lb/tons
6 | 20.5 | 4.11 | 500.57 | 84.351 | 85.05 | 1.09 | 83.96 | 20.405 | 463.62 | 396.67 | 603.45 | 817.06 | 100 | 139.83 | 420.39 | 14.1013 | 44.8522
7 | 22 | 4.11 | 500.36 | 90.4851 | 91.55 | 1.03 | 90.52 | 22.0085 | 409.7 | 551.35 | 558.08 | 965.4 | 100 | 148.38 | 414.05 | 13.1922 | 47.9428
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 111.7 | #DIV/0! | 111.7
2 | 71.8 |  | 71.8 | 63.8
3 | 62.5 |  | 62.5 | 60.1
4 | 50.9 |  | 50.9 | 45.3
5 | 33.5 |  | 33.5 | 31
6 | 30.1 |  | 30.1 | 27.1
7 | 32.8 |  | 32.8 | 31.7
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.139 | 1.1288 | 10 | 10 | 1.1473 | 1.1369 | 1 | 0.83 | 0.81 | 0.82 |  |  | 114730 | 113690 | 113690
2 | 1.1133 | 1.1124 | 10 | 10 | 1.1205 | 1.1194 | 1 | 0.72 | 0.7 | 0.71 |  |  | 112050 | 111940 | 111995
3 | 1.1168 | 1.136 | 10 | 10 | 1.1234 | 1.1421 | 1 | 0.66 | 0.61 | 0.635 |  |  | 112340 | 114210 | 113275
4 | 1.1255 | 1.114 | 10 | 10 | 1.1307 | 1.1194 | 1 | 0.52 | 0.54 | 0.53 |  |  | 113070 | 111940 | 111940
5 | 1.1156 | 1.1124 | 10 | 10 | 1.1204 | 1.1172 | 1 | 0.48 | 0.48 | 0.48 |  |  | 112040 | 111720 | 111720
6 | 1.0979 | 1.1007 | 10 | 10 | 1.102 | 1.105 | 1 | 0.41 | 0.43 | 0.42 |  |  | 110200 | 110500 | 110350
7 | 1.1024 | 1.1129 | 10 | 10 | 1.106 | 1.1163 | 1 | 0.36 | 0.34 | 0.35 |  |  | 110600 | 111630 | 111630
Plant Filterate | 1.1228 | 1.1262 | 10 | 10 | 1.1262 | 1.1291 | 1 | 0.34 | 0.29 | 0.315 |  |  | 112620 | 112910 | 112910
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 1.0176 | 1.0244 | 5.3281 | 5.3066 | 2.3729 | 2.2943 | 31.4418 | 29.6553 | 30.5486 |  |  | 44.5356 | 43.2348 | 43.8852
2 | 1.0049 | 0.9898 | 5.1601 | 5.1235 | 2.3064 | 2.3141 | 31.3222 | 32.0367 | 31.6794 |  |  | 44.6968 | 45.1664 | 44.9316
3 | 1.0006 | 1.0007 | 5.2533 | 5.2283 | 2.4045 | 2.3562 | 33.012 | 32.0631 | 32.5375 |  |  | 45.7712 | 45.0663 | 45.4188
4 | 0.9842 | 0.9801 | 5.209 | 5.2458 | 2.2987 | 2.2727 | 31.1139 | 30.3022 | 30.708 |  |  | 44.1294 | 43.3242 | 43.7268
5 | 0.9982 | 0.989 | 5.2482 | 5.2307 | 2.3172 | 2.2279 | 31.0353 | 29.2076 | 30.1215 |  |  | 44.1523 | 42.5928 | 43.3725
6 | 0.9874 | 0.9914 | 5.2336 | 5.2404 | 2.3937 | 2.3974 | 33.119 | 33.0901 | 33.1046 |  |  | 45.7372 | 45.7484 | 45.7428
7 | 1.0139 | 1.005 | 5.2105 | 5.2086 | 2.4332 | 2.3926 | 33.8202 | 33.0098 | 33.415 |  |  | 46.698 | 45.9356 | 46.3168
Plant Cake | 0.9957 | 0.9911 | 5.4936 | 5.4839 | 2.4986 | 2.3562 | 33.4134 | 30.3842 | 31.8988 |  |  | 45.482 | 42.9658 | 44.2239
Sludge | 0.9908 | 0.9915 | 5.2675 | 5.2759 | 1.1736 | 1.1637 | 4.2743 | 4.0192 | 4.1468 |  |  | 22.28 | 22.0569 | 22.1685
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.139 | 1.1288 | 10 | 10 |  |  | 1 | -113.9 | -112.88 | -113.39 |  |  | 0 | 0 | 0
2 | 1.1133 | 1.1124 | 10 | 10 |  |  | 1 | -111.33 | -111.24 | -111.285 |  |  | 0 | 0 | 0
3 | 1.1255 | 1.114 | 10 | 10 |  |  | 1 | -112.55 | -111.4 | -111.975 |  |  | 0 | 0 | 0
4 | 1.1156 | 1.1124 | 10 | 10 |  |  | 1 | -111.56 | -111.24 | -111.4 |  |  | 0 | 0 | 0
5 | 1.0979 | 1.1007 | 10 | 10 |  |  | 1 | -109.79 | -110.07 | -109.93 |  |  | 0 | 0 | 0
6 | 1.1024 | 1.1129 | 10 | 10 |  |  | 1 | -110.24 | -111.29 | -110.765
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.9612 |  | 111.7 | 30.5486 | 820 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 111.7 |  |  |  | 13.8968 | 31.6794 | 710 | 13.8968 | 31.6794 | 710 | 0 |  |  | 31.9277 | 2 | 13.8968 | 31.6794 | 710 | 1000 | 710 |  | 1 | 13.8968 | 31.6794 | 710 | 0 |  | 21.7762 | 33.415 | 350 | 4.1468 |  |  | 2
13.8968 |  | 71.8 | 31.6794 | 710 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 91.75 | 21.7439 | 10 | 1 | [7 empty] | 1 | 31.6794 | 1.3252 | 3 | [18 empty] | 1
15.4732 |  | 62.5 | 32.5375 | 635 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 67.15 | 6.9248 | 10 | 2 | [7 empty] | 1 | 32.5375 | 30.6025 | 1 | [18 empty] | 1
17.0205 |  | 50.9 | 30.708 | 530 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 56.7 | 10.2293 | 10 | 2 | [7 empty] | 1 | 30.708 |  | 1 | [18 empty] | 1
18.9046 |  | 33.5 | 30.1215 | 480 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 42.2 | 20.6161 | 10 | 1 | [7 empty] | 1 | 30.1215 |  | 2 | [18 empty] | 2
20.405 |  | 30.1 | 33.1046 | 420 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 31.8 | 5.3459 | 10 | 2 | [7 empty] | 1 | 33.1046 |  | 1 | [18 empty] | 1
22.0085 |  | 32.8 | 33.415 | 350 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 31.45 | -4.2925 | 10 | 2 | [7 empty] | 1 | 33.415 | 4.1506 | 1 | [18 empty] | 1
0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 16.4 | 100 | 10 | 2 | [10 empty] | 2 | [18 empty] | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 04_01_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 240:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B5 | Poly Loading (lb) | 414.3222 |  | Shampling time | 240:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.171 | Floc Poly Flow (gpm) | 13.7997 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 80.7 | Poly Floc Flow (mgd) | 0.019872 |  | BFP TS | %TS | 3.8655 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11621 |  | Polymer ratio setting | - | 0.171 | 0.171 | 0.171 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.6895 |  | Polymer dose | lb/tonTS | 22.119 | 15.6527 | 14.6861 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.8655 | BFP Sludge Loading (dtpd) | 17.879 |  | Cake TS | %TS | 32.7912 | 33.126 | 32.6566 | [11 empty] | Sampling time |  | 240:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 378 | Plant Polydose (Ib/ton) - method 1 | 23.1736 |  | Filtrate TSS | mg TSS/L | 325 | 560 | 700 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 207 | Plant Polydose (Ib/ton) - method 2 | 22.119
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.8655
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.171
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 22.119 | 15.6527 | 14.6861
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.7912 | 33.126 | 32.6566
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 325 | 560 | 700
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~22.15lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =18.95 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 11.5 | 3.8655 | 501.92 | 44.6234 | 47.51 | 0.66 | 46.85 | 12.0738 | 204.61 | 326.48 | 362.85 | 692.61 | 100 | 158.24 | 366.13 | 11.7157 | 53.9852
2 | 12.5 | 3.8655 | 502.99 | 48.6071 | 52.55 | 0.58 | 51.97 | 13.3648 | 406.35 | 399.1 | 551.72 | 782.21 | 100 | 145.37 | 383.11 | 12.7366 | 49.658
3 | 14 | 3.8655 | 502.48 | 54.3848 | 57.92 | 0.87 | 57.05 | 14.6861 | 205.92 | 413.2 | 357.65 | 775.8 | 100 | 151.73 | 362.6 | 11.767 | 53.7495 | [13 empty] | confirming that reducing polymer improves efficiency.
4 | 15 | 3.8655 | 501.53 | 58.1593 | 61.34 | 0.65 | 60.69 | 15.6527 | 447.4 | 361.85 | 591.73 | 742.8 | 100 | 144.33 | 380.95 | 12.5495 | 50.3983 | [13 empty] | - EPD < OPD < PD
5 | 16.5 | 3.8655 | 501.15 | 63.9267 | 67.8 | 0.66 | 67.14 | 17.3294 | 454.66 | 400.95 | 600.35 | 784.62 | 100 | 145.69 | 383.67 | 12.3857 | 51.0648 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
6 | 18 | 3.8655 | 500.48 | 69.645 | 73.53 | 0.75 | 72.78 | 18.8103 | 449.2 | 396.75 | 619.22 | 760.39 | 100 | 170.02 | 363.64 | 10.5926 | 59.7092 | [13 empty] | -0.33481 | lb/tons
7 | 20 | 3.8655 | 500.56 | 77.3957 | 81.63 | 0.67 | 80.96 | 20.9211 | 418.61 | 400.26 | 582.8 | 782.49 | 100 | 164.19 | 382.23 | 11.0732 | 57.1175
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 152.3 |  | 152.3 | 133.2
2 | 91.45 |  | 91.5 | 91.4
3 | 63.9 |  | 63.9 | 82 | 68
4 | 50 |  | 50 | 51.5
5 | 43.2 |  | 43.2 | 42.7
6 | 32.6 |  | 32.6 | 54 | 31.7
7 | 25.8 |  | 25.8 | 29 | 25.8
8 | 26 |  | 26 | 25.1
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1184 | 1.1147 | 10 | 10 | 1.1325 | 1.1226 | 1 | 1.41 | 0.79 | 1.1 |  |  | 113250 | 112260 | 112260
2 | 1.1267 | 1.1173 | 10 | 10 | 1.1342 | 1.1236 | 1 | 0.75 | 0.63 | 0.69 |  |  | 113420 | 112360 | 112890
3 | 1.1077 | 1.1212 | 10 | 10 | 1.1138 | 1.1291 | 1 | 0.61 | 0.79 | 0.7 |  |  | 111380 | 112910 | 112145
4 | 1.1082 | 1.1097 | 10 | 10 | 1.1138 | 1.1153 | 1 | 0.56 | 0.56 | 0.56 |  |  | 111380 | 111530 | 111530
5 | 1.1266 | 1.1228 | 10 | 10 | 1.1318 | 1.1277 | 1 | 0.52 | 0.49 | 0.505 |  |  | 113180 | 112770 | 112975
6 | 1.1167 | 1.1169 | 10 | 10 | 1.1213 | 1.1211 | 1 | 0.46 | 0.42 | 0.44 |  |  | 112130 | 112110 | 112110
7 | 1.1135 | 1.113 | 10 | 10 | 1.1168 | 1.1162 | 1 | 0.33 | 0.32 | 0.325 |  |  | 111680 | 111620 | 111650
Plant Filterate | 1.1219 | 1.1046 | 10 | 10 | 1.1284 | 1.1114 | 1 | 0.65 | 0.68 | 0.665 |  |  | 112840 | 111140 | 111140
8 | 1.1139 | 1.1197 | 10 | 10 | 1.1165 | 1.1224 | 1 | 0.26 | 0.27 | 0.265 |  |  | 111650 | 112240 | 112240
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9939 | 0.9969 | 5.2216 | 5.817 | 2.3751 | 2.4917 | 32.6702 | 31.0118 | 31.841 |  |  | 45.4861 | 42.8348 | 44.1604
2 | 0.9938 | 0.9929 | 5.1976 | 5.3002 | 2.318 | 2.3853 | 31.5001 | 32.3265 | 31.9133 |  |  | 44.5975 | 45.004 | 44.8007
3 | 0.9837 | 1.0051 | 5.3111 | 5.4597 | 2.3969 | 2.4598 | 32.657 | 32.6561 | 32.6566 |  |  | 45.13 | 45.0538 | 45.0919
4 | 0.9805 | 0.9883 | 5.0727 | 6.113 | 2.3503 | 2.6681 | 33.4734 | 32.7785 | 33.126 |  |  | 46.3323 | 43.6463 | 44.9893
5 | 0.9947 | 1.0043 | 5.2518 | 5.9504 | 2.4141 | 2.6272 | 33.3419 | 32.8117 | 33.0768 |  |  | 45.9671 | 44.1517 | 45.0594
6 | 0.9622 | 0.9899 | 5.5385 | 6.6473 | 2.4075 | 2.8281 | 31.5823 | 32.492 | 32.0371 |  |  | 43.4684 | 42.5451 | 43.0068
7 | 1.0077 | 1.0005 | 5.8681 | 6.3414 | 2.5987 | 2.7549 | 32.7339 | 32.8484 | 32.7912 |  |  | 44.2852 | 43.4431 | 43.8641
Plant Cake | 1.0048 | 0.9839 | 6.1289 | 6.1363 | 2.5052 | 2.5639 | 29.2812 | 30.6653 | 29.9733 |  |  | 40.8752 | 41.7825 | 41.3289
Sludge | 0.9923 | 0.9935 | 10.5532 | 10.9075 | 1.359 | 1.3797 | 3.8354 | 3.8955 | 3.8655 | 1.1269 | 1.1411 | 2.1993 | 2.1875 | 2.1934
8 | 0.9988 | 0.9951 | 5.3776 | 5.2628 | 2.4153 | 2.3719 | 32.349 | 32.2609 | 32.305
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 | 1.1093 |  | 10 | 10 | 1.1156 |  | 1 | 0.63 | 0 | 0.315 |  |  | 111560 | 0 | 0
3 | 1.1097 |  | 10 | 10 | 1.1153 |  | 1 | 0.56 | 0 | 0.28 |  |  | 111530 | 0 | 55765
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9944 |  | 5.0545 |  | 2.2168 |  | 30.1076 | #DIV/0! | #DIV/0! |  |  | 43.8579 | #DIV/0! | #DIV/0!
2 | 0.9786 |  | 6.7295 |  | 2.8278 |  | 32.155 | #DIV/0! | #DIV/0! |  |  | 42.021 | #DIV/0! | #DIV/0!
3 | 0.9852 |  | 5.9093 |  | 2.5875 |  | 32.54 | #DIV/0! | #DIV/0! |  |  | 43.7869 | #DIV/0! | #DIV/0!
4 | 1.013 |  | 5.6389 |  | 2.5649 |  | 33.5481 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 0.9987 |  | 6.063 |  | 2.69 |  | 33.3965 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6 | 0.9857 |  | 5.6166 |  | 2.4953 |  | 32.5984 | #REF! | #REF!
Plant Cake | 0.9684 |  | 6.0554 |  | 2.4691 |  | 29.5007 | #DIV/0! | #DIV/0! |  |  | 40.7752 | #DIV/0! | #DIV/0!
Sludge | 0.9925 |  | 10.9227 |  | 1.382 |  | 3.9224 | #DIV/0! | #DIV/0! | 1.1409 |  | 2.2073 | #DIV/0! | #DIV/0!
7 Cake | 1.0053 |  | 6.0175 |  | 2.6598 |  | 33.0095 | #DIV/0! | #DIV/0!
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.0738 |  | 152.3 | 31.841 | 1100 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 152.3 |  |  |  | 15.6527 | 33.126 | 560 | 15.6527 | 33.126 | 560 | 0 |  |  | 32.7578 | 2 | 14.6861 | 32.6566 | 700 | 1000 | 700 |  | 1 | 14.6861 | 32.6566 | 700 | 0 |  | 22.119 | 32.7912 | 325 | 3.8655 |  |  | 2
13.3648 |  | 91.45 | 31.9133 | 690 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 121.875 | 24.9641 | 10 | 2 | [9 empty] | 0.5026 | 2 | [18 empty] | 2
14.6861 |  | 63.9 | 32.6566 | 700 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 77.675 | 17.7341 | 10 | 2 | [9 empty] | 32.2552 | 3 | [18 empty] | 1
15.6527 |  | 50 | 33.126 | 560 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 56.95 | 12.2037 | 10 | 1 | [7 empty] | 1 | 33.126 |  | 1 | [18 empty] | 1
17.3294 |  | 43.2 | 33.0768 | 505 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 46.6 | 7.2961 | 10 | 2 | [7 empty] | 1 | 33.0768 |  | 1 | [18 empty] | 1
18.8103 |  | 32.6 | 32.0371 | 440 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 37.9 | 13.9842 | 10 | 2 | [7 empty] | 1 | 32.0371 |  | 2 | [18 empty] | 2
20.9211 |  | 25.8 | 32.7912 | 325 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 29.2 | 11.6438 | 10 | 1 | [7 empty] | 1 | 32.7912 | 1.5343 | 1 | [18 empty] | 1
21.9179 |  | 26 | 32.305 | 265 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 25.9 | -0.3861 | 10 | 2 | [7 empty] | 1 | 32.305 |  | 1 | [18 empty] | 1
8 | 22 | 4.04 | 501.76 | 89.1928 | 89.84 | 0.98 | 88.86 | 21.9179 | 459.68 | 363.7 | 599.56 | 764.72 | 100 | 139.88 | 401.02 | 13.2718 | 47.6553
`
Filtrate
8 | 1.1135 | 1.113 | 10 | 10 | 1.1168 | 1.1162 | 1 | 0.33 | 0.32 | 0.325 |  |  | 111680 | 111620 | 111650
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N43: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 03_28_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 371.8172 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 12.384 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 68.8 | Poly Floc Flow (mgd) | 0.017833 |  | BFP TS | %TS | 4.11 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.099072 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.71 | Calculated BFP TS (%) | 3.5622 |  | Polymer dose | lb/tonTS | 21.8978 | 18.6291 | 13.7656 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.11 | BFP Sludge Loading (dtpd) | 14.7165 |  | Cake TS | %TS | 32.5614 | 31.5129 | 31.7278 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 340 | Plant Polydose (Ib/ton) - method 1 | 25.2653 |  | Filtrate TSS | mg TSS/L | 405 | 615 | 830 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 205 | Plant Polydose (Ib/ton) - method 2 | 21.8978
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.11
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 21.8978 | 18.6291 | 13.7656
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 32.5614 | 31.5129 | 31.7278
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 405 | 615 | 830
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial overdosing condition (PD = ~22.15lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =18.95 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 13 | 4.11 | 500.95 | 53.5315 | 52.88 | 0.62 | 52.26 | 12.6912 | 204.59 | 399.12 | 362.03 | 758.35 | 100 | 157.44 | 359.23 | 12.2136 | 51.7842
2 | 14 | 4.11 | 500.65 | 57.6148 | 57.65 | 1 | 56.65 | 13.7656 | 404.51 | 404.51 | 618.04 | 792.5 | 100 | 213.53 | 387.99 | 10.4011 | 60.8084 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 17 | 4.11 | 500.5 | 69.9398 | 60.86 | 0.68 | 60.18 | 14.6277 | 205.86 | 365.36 | 353.16 | 778.6 | 100 | 147.3 | 413.24 | 13.9616 | 45.3009 | [13 empty] | - EPD < OPD < PD
4 | 19 | 4.11 | 501.2 | 78.2774 | 69.5 | 0.74 | 68.76 | 16.6899 | 449.17 | 397.15 | 612.88 | 770.83 | 100 | 163.71 | 373.68 | 11.8638 | 53.3112 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 20.5 | 4.11 | 500.29 | 84.3038 | 77.65 | 1.04 | 76.61 | 18.6291 | 454.65 | 367 | 614.72 | 753.14 | 100 | 160.07 | 386.14 | 12.1622 | 52.003 | [13 empty] | 3.2687 | lb/tons
6 | 22 | 4.11 | 502.9 | 90.9444 | 83.92 | 1.05 | 82.87 | 20.0468 | 406.36 | 1030.2 | 563.92 | 1416.63 | 100 | 157.56 | 386.43 | 12.1826 | 51.9159
7 | 15 | 4.11 | 501.64 | 61.8522 | 90.22 | 0.73 | 89.49 | 21.7025 | 384.54 | 938.58 | 605.34 | 1334.47 | 100 | 220.8 | 395.89 | 9.7413 | 64.9266
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 111.5 | #DIV/0! | 115.9 | 107.1
2 | 89 |  | 89 | 83.9
3 | 69.5 |  | 69.5 | 60.9
4 | 53.8 |  | 53.8 | 52.1
5 | 40.3 |  | 44.5 | 40.3
6 | 49.5 |  | 49.5 | 38.9
7 | 45.9 |  | 45.9 | 48.8
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1139 | 1.1044 | 10 | 10 | 1.1229 | 1.1136 | 1 | 0.9 | 0.92 | 0.91 |  |  | 112290 | 111360 | 111360
2 | 1.1118 | 1.1021 | 10 | 10 | 1.12 | 1.1105 | 1 | 0.82 | 0.84 | 0.83 |  |  | 112000 | 111050 | 111525
3 | 1.1119 | 1.1092 | 10 | 10 | 1.1195 | 1.117 | 1 | 0.76 | 0.78 | 0.77 |  |  | 111950 | 111700 | 111825
4 | 1.124 | 1.1175 | 10 | 10 | 1.1309 | 1.1241 | 1 | 0.69 | 0.66 | 0.675 |  |  | 113090 | 112410 | 112410
5 | 1.1025 | 1.1006 | 10 | 10 | 1.1085 | 1.1069 | 1 | 0.6 | 0.63 | 0.615 |  |  | 110850 | 110690 | 110690
6 | 1.1044 | 1.1118 | 10 | 10 | 1.1098 | 1.117 | 1 | 0.54 | 0.52 | 0.53 |  |  | 110980 | 111700 | 111340
7 | 1.1079 | 1.1059 | 10 | 10 | 1.1127 | 1.1111 | 1 | 0.48 | 0.52 | 0.5 |  |  | 111270 | 111110 | 111110
Plant Filterate | 1.1106 | 1.1024 | 10 | 10 | 1.1146 | 1.1065 | 1 | 0.4 | 0.41 | 0.405 |  |  | 111460 | 110650 | 110650
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9896 | 0.995 | 5.0589 | 5.1169 | 2.1995 | 2.2425 | 29.7324 | 30.2652 | 29.9988 |  |  | 43.4778 | 43.8254 | 43.6516
2 | 0.993 | 1.006 | 5.5833 | 5.5963 | 2.4577 | 2.4541 | 31.9086 | 31.547 | 31.7278 |  |  | 44.0188 | 43.8522 | 43.9355
3 | 1.002 | 0.9979 | 5.2063 | 5.0191 | 2.3057 | 2.2377 | 31.0087 | 30.8316 | 30.9202 |  |  | 44.2867 | 44.5837 | 44.4352
4 | 1.0044 | 0.9916 | 5.2004 | 5.1447 | 2.2823 | 2.2575 | 30.4552 | 30.4808 | 30.468 |  |  | 43.887 | 43.8801 | 43.8836
5 | 0.979 | 0.9835 | 5.1077 | 5.0775 | 2.2909 | 2.2629 | 31.7751 | 31.2506 | 31.5129 |  |  | 44.8519 | 44.5672 | 44.7095
6 | 0.9963 | 0.976 | 5.0092 | 5.1879 | 2.2893 | 2.3578 | 32.2211 | 32.807 | 32.5141 |  |  | 45.7019 | 45.4481 | 45.575
7 | 0.9937 | 0.9929 | 5.3289 | 5.2634 | 2.3411 | 2.3929 | 31.0805 | 32.783 | 31.9318 |  |  | 43.9321 | 45.463 | 44.6976
Plant Cake | 0.9925 | 0.9911 | 5.0518 | 5.0309 | 2.3176 | 2.3032 | 32.6436 | 32.4793 | 32.5614 |  |  | 45.8767 | 45.7811 | 45.8289
Sludge | 0.9913 | 0.9861 | 5.2036 | 5.19 | 1.1562 | 1.1674 | 3.9147 | 4.3127 | 4.1137 |  |  | 22.2192 | 22.4933 | 22.3562
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
12.6912 |  | 111.5 | 29.9988 | 910 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 111.5 |  |  |  | 18.6291 | 31.5129 | 615 | 18.6291 | 31.5129 | 615 | 0 |  |  | 31.9862 | 2 | 13.7656 | 31.7278 | 830 | 1000 | 830 |  | 1 | 13.7656 | 31.7278 | 830 | 0 |  | 21.8978 | 32.5614 | 405 | 4.1137 |  |  | 2
13.7656 |  | 89 | 31.7278 | 830 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 100.25 | 11.2219 | 10 | 2 | [9 empty] | 0.50282 | 3 | [18 empty] | 1
14.6277 |  | 69.5 | 30.9202 | 770 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 79.25 | 12.3028 | 10 | 2 | [9 empty] | 31.4834 | 2 | [18 empty] | 2
16.6899 |  | 53.8 | 30.468 | 675 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 61.65 | 12.7332 | 10 | 2 | [10 empty] | 2 | [18 empty] | 2
18.6291 |  | 40.3 | 31.5129 | 615 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.05 | 14.3464 | 10 | 1 | [7 empty] | 1 | 31.5129 |  | 1 | [18 empty] | 1
20.0468 |  | 49.5 | 32.5141 | 530 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 44.9 | -10.245 | 10 | 2 | [7 empty] | 1 | 32.5141 |  | 1 | [18 empty] | 1
21.7025 |  | 45.9 | 31.9318 | 500 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.7 | 3.7736 | 10 | 2 | [7 empty] | 1 | 31.9318 | 1.572 | 1 | [18 empty] | 1
0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 22.95 | 100 | 10 | 2 | [10 empty] | 2 | [18 empty] | 2
is EPD cake TS < than OPD cake TS or higher?
[28 empty] | 32.2229 |  | 31.8112
[28 empty] | 0.41176 |  |  | 1.0231
[8 empty] | ` | [18 empty] | error% | 1.2778 | (<10% to have valid data for EPD determination)
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 03_21_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 03/21/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B2 | Poly Loading (lb) | 489.091 |  | Shampling time | 8:00 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.18 | Floc Poly Flow (gpm) | 16.29 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 90.5 | Poly Floc Flow (mgd) | 0.023458 |  | BFP TS | %TS | 4.04 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.13032 |  | Polymer ratio setting | - | 0.18 | 0.18 | 0.18 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.5 | Calculated BFP TS (%) | 3.2602 |  | Polymer dose | lb/tonTS | 22.2772 | 20.7442 | 15.0212 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.04 | BFP Sludge Loading (dtpd) | 17.7169 |  | Cake TS | %TS | 31.7197 | 31.3234 | 30.4375 | [11 empty] | Sampling time |  | 8:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 262 | Plant Polydose (Ib/ton) - method 1 | 27.6058 |  | Filtrate TSS | mg TSS/L | 555 | 620 | 620 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 180 | Plant Polydose (Ib/ton) - method 2 | 22.2772
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.04
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.18
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 22.2772 | 20.7442 | 15.0212
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 31.7197 | 31.3234 | 30.4375
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 555 | 620 | 620
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~22.28lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =20.74 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 12.5 | 4.04 | 500.49 | 50.5495 | 51.96 | 1.01 | 50.95 | 12.599 | 204.72 | 399.08 | 370.14 | 739.65 | 100 | 165.42 | 340.57 | 11.2159 | 56.3909
2 | 15 | 4.04 | 501.85 | 60.8242 | 61.87 | 0.96 | 60.91 | 15.0212 | 206.97 | 401.08 | 362.27 | 761.48 | 100 | 155.3 | 360.4 | 11.9635 | 52.8669 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 16 | 4.04 | 502.2 | 64.9244 | 65.69 | 0.55 | 65.14 | 16.0531 | 465.97 | 405.85 | 635.18 | 768.35 | 100 | 169.21 | 362.5 | 11.2373 | 56.2831 | [13 empty] | - EPD < OPD < PD
4 | 17 | 4.04 | 500.51 | 68.75 | 69.85 | 0.96 | 68.89 | 17.0346 | 455.76 | 355.15 | 611.7 | 724.52 | 100 | 155.94 | 369.37 | 11.9629 | 52.8697 | [13 empty] | - We can achieve cost savings by operating at OPD instead of PD.
5 | 19 | 4.04 | 501.35 | 76.9672 | 77.15 | 1.31 | 75.84 | 18.7217 | 447.54 | 684.7 | 614.05 | 1045.65 | 100 | 166.51 | 360.95 | 11.1161 | 56.8969 | [13 empty] | 1.533 | lb/tons
6 | 20.5 | 4.04 | 501.81 | 83.1198 | 85.21 | 1.1 | 84.11 | 20.7442 | 411.5 | 946.5 | 553.74 | 1337.12 | 100 | 142.24 | 390.62 | 12.9621 | 48.7942
7 | 22.3 | 4.04 | 500.98 | 90.2686 | 92.95 | 1.3 | 91.65 | 22.6413 | 454.75 | 397.11 | 618.39 | 787.43 | 100 | 163.64 | 390.32 | 11.5613 | 54.7059
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 230.2 | #DIV/0! | 230.2
2 | 201.6 | 15 | 201.6
3 | 95.4 | 16 | 95.4 | 97.6
4 | 68.6 | 17 | 68.6
5 | 55.2 | 19 |  | 55.2 | 54.8
6 | 39.6 | 20.5 | 40.1 | 39.6
7 | 43.3 | 22.3 | 43.3 | 41.2
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1199 | 1.115 | 10 | 10 | 1.129 | 1.124 | 1 | 0.91 | 0.9 | 0.905 |  |  | 112900 | 112400 | 112400
2 | 1.1103 | 1.0958 | 10 | 10 | 1.1189 | 1.1048 | 1 | 0.86 | 0.9 | 0.88 |  |  | 111890 | 110480 | 111185
3 | 1.1188 | 1.1129 | 10 | 10 | 1.126 | 1.1199 | 1 | 0.72 | 0.7 | 0.71 |  |  | 112600 | 111990 | 111990
4 | 1.1142 | 1.101 | 10 | 10 | 1.1208 | 1.1078 | 1 | 0.66 | 0.68 | 0.67 |  |  | 112080 | 110780 | 110780
5 | 1.1168 | 1.1157 | 10 | 10 | 1.1229 | 1.122 | 1 | 0.61 | 0.63 | 0.62 |  |  | 112290 | 112200 | 112245
6 | 1.1221 | 1.1209 | 10 | 10 | 1.1274 | 1.126 | 1 | 0.53 | 0.51 | 0.52 |  |  | 112740 | 112600 | 112600
7 | 1.118 | 1.127 | 10 | 10 | 1.1236 | 1.1325 | 1 | 0.56 | 0.55 | 0.555 |  |  | 112360 | 113250 | 113250
Plant Filterate | 1.122 | 1.1104 | 10 | 10 | 1.1266 | 1.1149 | 1 | 0.46 | 0.45 | 0.455 |  |  | 112660 | 111490 | 111490
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9956 | 0.9921 | 5.2994 | 5.2906 | 2.2528 | 2.2587 | 29.2114 | 29.4661 | 29.3387 |  |  | 42.5105 | 42.6927 | 42.6016
2 | 0.9959 | 0.9972 | 5.2544 | 5.1435 | 2.2578 | 2.239 | 29.6325 | 29.9496 | 29.791 |  |  | 42.9697 | 43.5307 | 43.2502
3 | 1.0007 | 0.988 | 5.4308 | 5.2054 | 2.3657 | 2.2975 | 30.8119 | 31.0499 | 30.9309 |  |  | 43.5608 | 44.1369 | 43.8488
4 | 1.0016 | 0.9963 | 5.2364 | 5.3712 | 2.3445 | 2.402 | 31.7111 | 32.131 | 31.921 |  |  | 44.7731 | 44.72 | 44.7466
5 | 0.9999 | 0.9976 | 5.3014 | 5.4413 | 2.3036 | 2.3559 | 30.308 | 30.5669 | 30.4375 |  |  | 43.4527 | 43.2966 | 43.3747
6 | 0.9802 | 1.0136 | 5.307 | 5.2592 | 2.3264 | 2.3524 | 31.1131 | 31.5338 | 31.3234 |  |  | 43.8364 | 44.7292 | 44.2828
7 | 0.9787 | 0.9908 | 5.105 | 5.119 | 2.2941 | 2.2937 | 31.8784 | 31.561 | 31.7197 |  |  | 44.9383 | 44.8076 | 44.8729
Plant Cake | 1.0043 | 0.9936 | 5.4299 | 5.4103 | 2.4602 | 2.4381 | 32.8972 | 32.7054 | 32.8013 |  |  | 45.3084 | 45.064 | 45.1862
Sludge | 0.9985 | 1.0027 | 5.2777 | 5.432 | 1.1702 | 1.1827 | 4.0124 | 4.0638 | 4.0381 |  |  | 22.1725 | 21.7728 | 21.9727
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
4 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
6 | [6 empty] | #DIV/0! | #REF! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
7 Cake
7 Filtrate
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD determination | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked
12.599 |  | 230.2 | 29.3387 | 905 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 230.2 |  |  |  | 20.7442 | 31.3234 | 620 | 20.7442 | 31.3234 | 620 | 0 |  |  | 32.0624 | 2 | 15.0212 | 30.4375 | 620 | 1000 | 620 |  | 1 | 15.0212 | 30.4375 | 620 | 0 |  | 22.2772 | 31.7197 | 555 | 32.8013
15.0212 |  | 201.6 | 29.791 | 880 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 215.9 | 6.6234 | 10 | 2 | [9 empty] | 1.045 | 3 | [17 empty] | 1
16.0531 |  | 95.4 | 30.9309 | 710 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 148.5 | 35.7576 | 10 | 2 | [9 empty] | 31.0174 | 2 | [16 empty] | 1
17.0346 |  | 68.6 | 31.921 | 670 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 82 | 16.3415 | 10 | 2 | [10 empty] | 3
18.7217 |  | 55.2 | 30.4375 | 620 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 61.9 | 10.8239 | 10 | 2 | [10 empty] | 1
20.7442 |  | 39.6 | 31.3234 | 520 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.4 | 16.4557 | 10 | 1 | [7 empty] | 1 | 31.3234 |  | 1
22.6413 |  | 43.3 | 32.8013 | 555 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 41.45 | -4.4632 | 10 | 2 | [7 empty] | 1 |  | 3.2593 | 1
Haydee's calculations
is EPD cake TS < than OPD cake TS or higher?
[28 empty] | 31.0965 |  | 30.341
[28 empty] | 0.75552 |  |  | 0.74645
[8 empty] | ` | [18 empty] | error% | 2.4296 | (<10% to have valid data for EPD determination)
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE97: Hua G. Chieu (CTR): Average of all Cake TS after OPD point.
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 02_28_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 02/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 8:30 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B2 | Poly Loading (lb) | 375.7083 |  | Shampling time | 8:30 |  |  |  | Parnia | 1 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.158 | Floc Poly Flow (gpm) | 12.5136 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 0
Sludge Flow (gpm) | 79.2 | Poly Floc Flow (mgd) | 0.01802 |  | BFP TS | %TS | 4.26 |  |  | Tu Duong | 0 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11405 |  | Polymer ratio setting | - | 0.158 | 0.158 | 0.158 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.5 | Calculated BFP TS (%) | 3.6441 |  | Polymer dose | lb/tonTS | 18.5446 | 14.7019 | 14.7019 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 4.26 | BFP Sludge Loading (dtpd) | 17.3306 |  | Cake TS | %TS | 30.2463 | 30.3493 | 30.3493 | [11 empty] | Sampling time |  | 8:30 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 269 | Plant Polydose (Ib/ton) - method 1 | 21.6789 |  | Filtrate TSS | mg TSS/L | 525 | 695 | 695 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 137 | Plant Polydose (Ib/ton) - method 2 | 18.5446
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 4.26
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.158
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 18.5446 | 14.7019 | 14.7019
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 30.2463 | 30.3493 | 30.3493
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 525 | 695 | 695
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~18.54lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =16.55 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 14 | 4.26 | 501.54 | 59.8237 | 51.29 | 0.53 | 50.76 | 11.8789 | 204.54 | 399.07 | 358.92 | 768.09 | 100 | 154.38 | 369.02 | 13.1154 | 48.2235 | [13 empty] | confirming that reducing polymer improves efficiency.
2 | 16 | 4.26 | 500.4 | 68.2145 | 63.24 | 0.56 | 62.68 | 14.7019 | 205.86 | 361.74 | 357.7 | 746.57 | 100 | 151.84 | 384.83 | 13.3807 | 47.2676 | [13 empty] | - EPD < OPD < PD
3 | 18 | 4.26 | 500.69 | 76.7858 | 71.27 | 0.69 | 70.58 | 16.5452 | 449.06 | 397.15 | 596.64 | 795.51 | 100 | 147.58 | 398.36 | 13.8119 | 45.7917 | [13 empty] | - We can achieve cost savings by operating at EPD instead of PD.
4 | 20.5 | 4.26 | 500.72 | 87.4557 | 80.8 | 0.75 | 80.05 | 18.7641 | 447.29 | 684.65 | 586.47 | 1103.53 | 100 | 139.18 | 418.88 | 14.7267 | 42.9474 | [13 empty] | 3.8427 | lb/tons
5 | 25 | 4.26 | 500.11 | 106.5234 | 98.28 | 0.58 | 97.7 | 22.9292 | 406.43 | 978.7 | 552.08 | 1398.7 | 100 | 145.65 | 420 | 13.8404 | 45.6975
6
7
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 116.4 | #DIV/0! | 116.4
2 | 51 | #DIV/0! | 51
3 | 44 | #DIV/0! | 48 | 44
4 | 51.4 | #DIV/0! | 50.6 | 52.2
5 | 54 | #DIV/0! | 52 | 56
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1098 | 1.1226 | 10 | 10 | 1.12 | 1.1329 | 1 | 1.02 | 1.03 | 1.025 |  |  | 112000 | 113290 | 113290
2 | 1.1167 | 1.1109 | 10 | 10 | 1.1237 | 1.1178 | 1 | 0.7 | 0.69 | 0.695 |  |  | 112370 | 111780 | 112075
3 | 1.1067 | 1.1204 | 10 | 10 | 1.112 | 1.126 | 1 | 0.53 | 0.56 | 0.545 |  |  | 111200 | 112600 | 111900
4 | 1.1053 | 1.1101 | 10 | 10 | 1.1106 | 1.1155 | 1 | 0.53 | 0.54 | 0.535 |  |  | 111060 | 111550 | 111550
5 | 1.1112 | 1.1099 | 10 | 10 | 1.1144 | 1.113 | 1 | 0.32 | 0.31 | 0.315 |  |  | 111440 | 111300 | 111300
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0
Plant Filterate | 1.1245 | 1.117 | 10 | 10 | 1.13 | 1.122 | 1 | 0.55 | 0.5 | 0.525 |  |  | 113000 | 112200 | 112200
.
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9807 | 0.9986 | 5.0831 | 5.0613 | 2.208 | 2.1695 | 29.9166 | 28.8207 | 29.3687 |  |  | 43.4381 | 42.8645 | 43.1513
2 | 0.996 | 1.0014 | 5.1687 | 5.1679 | 2.2699 | 2.2584 | 30.5294 | 30.1692 | 30.3493 |  |  | 43.9163 | 43.7005 | 43.8084
3 | 1.0045 | 0.99 | 5.0603 | 5.0387 | 2.2892 | 2.2045 | 31.6756 | 29.9973 | 30.8365 |  |  | 45.2384 | 43.7514 | 44.4949
4 | 0.9803 | 0.9897 | 5.0503 | 5.079 | 2.2145 | 2.2205 | 30.3243 | 30.0981 | 30.2112 |  |  | 43.8489 | 43.7192 | 43.7841
5 | 1.0045 | 0.9938 | 5.0312 | 5.0832 | 2.229 | 2.252 | 30.4095 | 30.7673 | 30.5884 |  |  | 44.3035 | 44.3028 | 44.3032
6 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 1.0015 | 1.003 | 5.0995 | 5.0819 | 2.2392 | 2.2385 | 30.2025 | 30.29 | 30.2463 |  |  | 43.9102 | 44.0485 | 43.9793
Sludge | 1.0007 | 0.9796 | 5.4339 | 5.4106 | 1.1865 | 1.1714 | 4.1911 | 4.3286 | 4.2598 |  |  | 21.8351 | 21.6501 | 21.7426
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #3 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
4 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
6 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD Indication Point (3) | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked | EPD determination
11.8789 | #DIV/0! | 116.4 | 29.3687 | 1025 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 116.4 |  |  |  | 14.7019 | 30.3493 | 695 | 14.7019 | 30.3493 | 695 | 0 |  |  | 30.4963 | 2 | 14.7019 | 30.3493 | 695 | 1000 | 695 |  | 1 | 14.7019 | 30.3493 | 695 | 0 |  | 18.5446 | 30.2463 | 525 | 4.2598 |  |  | 2
14.7019 | #DIV/0! | 51 | 30.3493 | 695 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 83.7 | 39.0681 | 10 | 1 | [7 empty] | 1 | 30.3493 | 0.27513 | 3 | [18 empty] | 1
16.5452 | #DIV/0! | 44 | 30.8365 | 545 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.5 | 7.3684 | 10 | 2 | [7 empty] | 1 | 30.8365 | 30.2212 | 1 | [18 empty] | 1
18.7641 | #DIV/0! | 51.4 | 30.2112 | 535 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 47.7 | -7.7568 | 10 | 2 | [7 empty] | 1 | 30.2112 |  | 2 | [18 empty] | 2
22.9292 | #DIV/0! | 54 | 30.5884 | 315 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 52.7 | -2.4668 | 10 | 2 | [7 empty] | 1 | 30.5884 |  | 1 | [18 empty] | 1
[31 empty] | 2 | [18 empty] | 2
[30 empty] | 0.90217 | 2 | [18 empty] | 2
[27 empty] | Haydee's calculations |  |  |  | 2 | [18 empty] | 2
is EPD cake TS < than OPD cake TS or higher?
[28 empty] | 30.5454 |  | 30.2305
[28 empty] | 0.31485 |  |  | 0.26675
[8 empty] | ` | [18 empty] | error% | 1.0308 | (<10% to have valid data for EPD determination)
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N41: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 02_18_2025_Standard_Nam
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 02/07/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 9:30 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | A2 | Poly Loading (lb) | 415.5562 |  | Shampling time | 9:30 |  |  |  | Parnia | 0 |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.158 | Floc Poly Flow (gpm) | 13.8408 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 87.6 | Poly Floc Flow (mgd) | 0.019931 |  | BFP TS | %TS | 3.3801 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.12614 |  | Polymer ratio setting | - | 0.158 |  |  | Nam Ngo | 1
SBT3 TS % LAB_TSPCT_J04 | 5.2 | Calculated BFP TS (%) | 3.2791 |  | Polymer dose | lb/tonTS | 23.3723 | 21.4636 | 16.5585 | Haydee | 1 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.3801 | BFP Sludge Loading (dtpd) | 17.2485 |  | Cake TS | %TS | 30.5721 | 31.3953 | 31.7232 | [11 empty] | Sampling time |  | 9:30 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 268 | Plant Polydose (Ib/ton) - method 1 | 24.0923 |  | Filtrate TSS | mg TSS/L | 370 | 555 | 715 | [11 empty] | Analyzer |  | Hung and Tu | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 157 | Plant Polydose (Ib/ton) - method 2 | 23.3723
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.3801
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.158
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 23.3723 | 21.4636 | 16.5585
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 30.5721 | 31.3953 | 31.7232
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 370 | 555 | 715
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
Calculation
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g)
1 | 16 | 3.3801 | 500.1 | 54.0919 | 56.84 | 0.86 | 55.98 | 16.5585 | 447.27 | 339.01 | 593.28 | 776.2 | 100 | 146.01 | 437.19 | 12.1417 | 52.0909
2 | 18 | 3.3801 | 500.39 | 60.8886 | 64.19 | 0.83 | 63.36 | 18.7306 | 205.81 | 407.83 | 356.89 | 787.46 | 100 | 151.08 | 379.63 | 10.539 | 60.0128
3 | 20.5 | 3.3801 | 500.77 | 69.3981 | 73.66 | 1 | 72.66 | 21.4636 | 204.53 | 403.97 | 359.85 | 786.46 | 100 | 155.32 | 382.49 | 10.2208 | 61.8809
4 | 22.5 | 3.3801 | 500.8 | 76.1732 | 80.23 | 0.89 | 79.34 | 23.4354 | 454.57 | 397.21 | 595.24 | 800.92 | 100 | 140.67 | 403.71 | 11.2917 | 56.0124
5 | 25 | 3.3801 | 500.94 | 84.6605 | 89.46 | 0.82 | 88.64 | 26.1751 | 449.02 | 397.68 | 605.79 | 797.34 | 100 | 156.77 | 399.66 | 10.1933 | 62.0477
6
7
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 128.6 | 55.4 | 128.6 |  |  |  |  | 55.4
2 | 50.2 | 38.7 | 50.2 |  |  |  |  | 38.7
3 | 40.2 | 25.9 | 40.2 |  |  |  |  | 25.9
4 | 42.3 | 27.5 | 42.3 | 52.9 |  |  |  | 27.5
5 | 40.6 | 34.6 | 40.6 |  |  |  |  | 34.6
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1248 | 1.1104 | 10 | 10 | 1.1317 | 1.1178 | 1 | 0.69 | 0.74 | 0.715 |  |  | 113170 | 111780 | 111780
2 | 1.0997 | 1.1114 | 10 | 10 | 1.1054 | 1.1168 | 1 | 0.57 | 0.54 | 0.555 |  |  | 110540 | 111680 | 111110
3 | 1.1148 | 1.1157 | 10 | 10 | 1.1202 | 1.121 | 1 | 0.54 | 0.53 | 0.535 |  |  | 112020 | 112100 | 112060
4 | 1.1249 | 1.1103 | 10 | 10 | 1.1292 | 1.1145 | 1 | 0.43 | 0.42 | 0.425 |  |  | 112920 | 111450 | 111450
5 | 1.1158 | 1.1179 | 10 | 10 | 1.1192 | 1.1212 | 1 | 0.34 | 0.33 | 0.335 |  |  | 111920 | 112120 | 112120
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0
Plant Filterate | 1.1153 | 1.109 | 10 | 10 | 1.1192 | 1.1125 | 1 | 0.39 | 0.35 | 0.37 |  |  | 111920 | 111250 | 111250
.
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 0.9836 | 1.0088 | 6.3319 | 5.0082 | 2.6894 | 2.2707 | 31.8942 | 31.5522 | 31.7232 |  |  | 42.4738 | 45.3396 | 43.9067
2 | 0.9811 | 0.9928 | 6.3937 | 5.766 | 2.7258 | 2.3895 | 32.234 | 29.2613 | 30.7477 |  |  | 42.6326 | 41.4412 | 42.0369
3 | 0.9889 | 0.9781 | 6.2951 | 5.343 | 2.6527 | 2.3502 | 31.3558 | 31.4349 | 31.3953 |  |  | 41.8843 | 40.7596 | 41.322
4 | 0.9961 | 0.9972 | 6.3334 | 6.5387 | 2.6798 | 2.7416 | 31.5459 | 31.4788 | 31.5124 |  |  | #DIV/0! | 51.312 | #DIV/0!
5 | 0.9992 | 0.977 | 5.0516 | 5.227 | 2.3044 | 2.4001 | 32.2081 | 33.4847 | 32.8464 |  |  | 45.6172 | 45.9174 | 45.7673
6 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | 1.0016 | 0.9957 | 6.6065 | 5.4766 | 2.7199 | 2.3618 | 30.6571 | 30.4872 | 30.5721 |  |  | 41.1701 | 43.1253 | 42.1477
Sludge | 1.0042 | 0.9933 | 9.9281 | 9.9211 | 1.3044 | 1.2965 | 3.364 | 3.3961 | 3.3801 |  |  | 13.1385 | 13.0681 | 13.1033
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #3 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0
Plant Filterate |  |  | 10 | 10 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
3 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
4 | [6 empty] | #DIV/0! | #REF! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
6 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Plant Cake | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Sludge | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Ave | Diff | Tolerance (%) | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked
16.5585 | 55.4 | 128.6 | 31.7232 | 715 | 55.4 | 0 | 10 |  | 21.4636 | 30.7477 | 555 | 21.4636 | 30.7477 | 555 | 0 |  | 128.6 |  |  |  | 21.4636 | 31.3953 | 555 | 21.4636 | 31.3953 | 555 | 0 | 31.7232 | 0 | 0 |  | #N/A | #N/A | #N/A | 812 | #N/A |  | #N/A | 16.5585 | 31.7232 | 715 | 1 |  | 23.3723 | 30.5721 | 370 | 3.3801 |  | 1
18.7306 | 38.7 | 50.2 | 30.7477 | 555 | 47.05 | 17.7471 | 10 | 2 | [8 empty] | 89.4 | 43.8479 | 10 | 2 | [7 empty] | 31.2355 | 1.5616 | 1 | 2
21.4636 | 25.9 | 40.2 | 31.3953 | 535 | 32.3 | 19.8142 | 10 | 1 | [8 empty] | 45.2 | 11.0619 | 10 | 1 | [7 empty] | 31.0715 | -1.0422 | 1 | 2
23.4354 | 27.5 | 42.3 | 31.5124 | 425 | 26.7 | -2.9963 | 10 | 2 | [8 empty] | 41.25 | -2.5455 | 10 | 2 | [7 empty] | 31.4538 | -0.18609 | 1 | 2
26.1751 | 34.6 | 40.6 | 32.8464 | 335 | 31.05 | -11.4332 | 10 | 2 | [8 empty] | 41.45 | 2.0507 | 10 | 2 | [7 empty] | 32.1794 | -2.0728 | 1 | 2
`
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N41: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g

## 03_18_2025
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 02/28/2025
Plant Data Conversion |  |  |  |  | Summary Table
Shampling time | 10:00 | [8 empty] | Data QAQC Name | Data QAQC (yes/No) | Comment | Notes: first round, we'll do the QA/AC with first 25 tabs
Belt No. | B2 | Poly Loading (lb) | 392.0954 |  | Shampling time | 10:00 |  |  |  | Parnia |  |  | from the tab 2_21_2025 to 8_20_2024
Poly Ratio | 0.167 | Floc Poly Flow (gpm) | 13.0594 |  |  | unit | Plant | OPD | EPD | Hung Chieu | 1
Sludge Flow (gpm) | 78.2 | Poly Floc Flow (mgd) | 0.018806 |  | BFP TS | %TS | 3.5 |  |  | Tu Duong | 1 | [9 empty] | Test Details | [12 empty] | Target table
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11261 |  | Polymer ratio setting | - | 0.167 | 0.167 | 0.167 | Nam Ngo | 0
SBT3 TS % LAB_TSPCT_J04 | 5.5 | Calculated BFP TS (%) | 3.587 |  | Polymer dose | lb/tonTS | 23.8571 | 19.3161 | 15.2225 | Haydee | 0 | [23 empty] | BFP TS | Filtrate TS
BFP TS % | 3.5 | BFP Sludge Loading (dtpd) | 16.8435 |  | Cake TS | %TS | 30.4793 | 31.8388 | 32.0828 | [11 empty] | Sampling time |  | 10:00 | [10 empty] | Unit | % | mg TSS/L
DIG SLDG FLOW FROM SBT (gpm) | 270 | Plant Polydose (Ib/ton) - method 1 | 23.2788 |  | Filtrate TSS | mg TSS/L | 375 | 640 | 795 | [11 empty] | Analyzer |  | Parnia | [11 empty] | 3 - 3.9 | < 812
DIL WTR FLOW TO BFP (gpm) | 144 | Plant Polydose (Ib/ton) - method 2 | 23.8571
Summary Table
Assumptions and Constants:
[31 empty] | Details |  |  |  | batch testing
1 g = | 0.0022046 | lb | [30 empty] | unit | Plant | OPD | EPD
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches | [28 empty] | BFP TS |  | %TS | 3.5
Cup Area: | 0.0079059 | m2 | [28 empty] | Polymer ratio setting |  | vol/vol | 0.167
Aiming for 0.80 kg of DS per m2 of cup area | [30 empty] | Polymer dose |  | lb/tonTS | 23.8571 | 19.3161 | 15.2225
Cup Loading | 6.3247 | grams of DS | [28 empty] | Cake TS |  | %TS | 30.4793 | 31.8388 | 32.0828
Assuming | 3.5 | TS in sludge | [28 empty] | Filtrate TSS |  | mg TSS/L | 375 | 640 | 795
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m | [28 empty] | Remarks:
- Based on the initial a little bit overdosing condition (PD = ~18.54lb/ton)
need to decrease the polymer ratio
Calculation | [30 empty] | - Based on the graph, the OPD =16.55 < PD
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g) | [13 empty] | Conclusion: Experiment results are consistent with expectations.
1 | 12.5 | 3.5 | 500.43 | 43.7876 | 45.12 | 0.7 | 44.42 | 12.6805 | 454.65 | 686.5 | 591.44 | 700.55 | 100 | 136.79 | 14.05 | 3.5448 | 178.4206
2 | 15 | 3.5 | 500.2 | 52.521 | 54.05 | 0.75 | 53.3 | 15.2225 | 449.1 | 399.12 | 590.25 | 758.25 | 100 | 141.15 | 359.13 | 11.2105 | 56.4177 | [13 empty] | confirming that reducing polymer improves efficiency.
3 | 17 | 3.5 | 500.03 | 59.5036 | 61.06 | 0.82 | 60.24 | 17.2104 | 406.27 | 400.99 | 550.25 | 784.75 | 100 | 143.98 | 383.76 | 11.4494 | 55.2404 | [13 empty] | - EPD < OPD < PD
4 | 19 | 3.5 | 500.25 | 66.5332 | 68.45 | 0.81 | 67.64 | 19.3161 | 204.68 | 326.43 | 350.94 | 678.38 | 100 | 146.26 | 351.95 | 10.5021 | 60.2232 | [13 empty] | - We can achieve cost savings by operating at EPD instead of PD.
5 | 20.5 | 3.5 | 500.23 | 71.783 | 73.63 | 0.81 | 72.82 | 20.7962 | 205.9 | 325.31 | 346.82 | 708.39 | 100 | 140.92 | 383.08 | 11.3607 | 55.6721 | [13 empty] | -1.6035 | lb/tons
6 | 21.5 | 3.5 | 500.05 | 75.2575 | 77.28 | 1.02 | 76.26 | 21.7864 | 159.42 | 408.18 | 306.9 | 805.49 | 100 | 147.48 | 397.31 | 11.2182 | 56.3794
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 120.8 | #DIV/0! | 120.8
2 | 73.1 | #DIV/0! | 68.8 | 73.1
3 | 55.9 | #DIV/0! | 65.5 | 55.9
4 | 45.4 | #DIV/0! | 51.5 | 45.4
5 | 38.1 | #DIV/0! | 29.7 | 30 | 38.1
6 | 39.7 |  | 39.7
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1115 | 1.1165 | 10 | 10 | 1.1192 | 1.1247 | 1 | 0.77 | 0.82 | 0.795 |  |  | 111920 | 112470 | 112470
3 | 1.1085 | 1.1193 | 10 | 10 | 1.1152 | 1.1261 | 1 | 0.67 | 0.68 | 0.675 |  |  | 111520 | 112610 | 112065
2 | 1.1208 | 1.1096 | 10 | 10 | 1.1272 | 1.116 | 1 | 0.64 | 0.64 | 0.64 |  |  | 112720 | 111600 | 111600
4 | 1.1136 | 1.1159 | 10 | 10 | 1.1189 | 1.1216 | 1 | 0.53 | 0.57 | 0.55 |  |  | 111890 | 112160 | 112025
5 | 1.1114 | 1.1192 | 10 | 10 | 1.1154 | 1.124 | 1 | 0.4 | 0.48 | 0.44 |  |  | 111540 | 112400 | 112400
6 | 1.1102 | 1.1106 | 10 | 10 | 1.1146 | 1.115 | 1 | 0.44 | 0.44 | 0.44 |  |  | 111460 | 111500 | 111500
Plant Filterate | 1.115 | 1.1216 | 10 | 10 | 1.1188 | 1.1253 | 1 | 0.38 | 0.37 | 0.375 |  |  | 111880 | 112530 | 112530
TS - VS
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%)
1 | 1.0045 | 0.9879 | 5.7395 | 5.4818 | 2.5199 | 2.4332 | 32.0042 | 32.1614 | 32.0828 |  |  | 43.9045 | 44.3869 | 44.1457
2 | 0.9859 | 0.9985 | 6.0491 | 6.43 | 2.6355 | 2.7649 | 32.5802 | 32.5214 | 32.5508 |  |  | 43.5685 | 43 | 43.2842
3 | 0.9885 | 0.997 | 6.0865 | 6.0671 | 2.6398 | 2.6334 | 32.3911 | 32.2755 | 32.3333 |  |  | 43.3714 | 43.4046 | 43.388
4 | 0.9899 | 1.0212 | 5.1554 | 6.4198 | 2.3229 | 2.7313 | 32.001 | 31.6767 | 31.8388 |  |  | 39.565 | 45.0182 | 42.2916
5 | 1.004 | 0.9992 | 5.8711 | 6.3391 | 2.5495 | 2.7003 | 31.754 | 31.8564 | 31.8052 |  |  | 43.4246 | 42.0621 | 42.7433
| 0.991 | 1.004 | 6.1707 | 5.8765 | 2.6642 | 2.5871 | 32.303 | 32.4905 | 32.3968
Plant Cake | 1.0302 | 0.9913 | 5.3262 | 5.0174 | 2.3297 | 2.2277 | 30.2491 | 30.7096 | 30.4793 |  |  | 43.7404 | 44.3995 | 44.0699
Sludge | 0.9972 | 1.0051 | 10.4413 | 10.5265 | 1.3299 | 1.3364 | 3.5228 | 3.4795 | 3.5012 |  | 1.1215 |  | 2.0415 | 2.0415
Additional experiement
TSS - VSS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%)
1 | 1.1137 |  | 10 | 10 | 1.1214 |  | 1 | 0.77 | 0 | 0.385 |  |  | 112140 | 0 | 0
2 | 1.1159 |  | 10 | 10 | 1.1216 |  | 1 | 0.57 | 0 | 0.285 |  |  | 112160 | 0 | 0
3 | 1.1122 |  | 10 | 10 | 1.1191 |  | 1 | 0.69 | 0 | 0.345 |  |  | 111910 | 0 | 55955
4 | 1.1252 |  | 10 | 10 | 1.1316 |  | 1 | 0.64 | 0 | 0.32 |  |  | 113160 | 0 | 56580
5 | 1.1227 |  | 10 | 10 | 1.127 |  | 1 | 0.43 | 0 | 0.215 |  |  | 112700 | 0 | 0
6 | 1.1102 |  | 10 | 10 | 1.1146 |  | 1 | 0.44 | 0 | 0.22
Plant Filterate | 1.1118 |  | 10 | 10 | 1.1159 |  | 1 | 0.41 | 0 | 0.205 |  |  | 111590 | 0 | 0
TS - VS
Sample ID/# | Foil Tray (g) #3 | Foil Tray (g) #2 | Tray +Sample (g) #3 | Tray + Sample (g) #2 | After 103 °C #3 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 |  | VS-1 (%) | VS-2 (%) | VS (%)
1 | 1.0045 |  | 5.7395 |  | 2.5199 |  | 32.0042 | #DIV/0! | #DIV/0! |  |  | 43.9045 | #DIV/0! | #DIV/0!
2 | 0.9985 |  | 6.43 |  | 2.7649 |  | 32.5214 | #DIV/0! | #DIV/0! |  |  | 43 | #DIV/0! | #DIV/0!
3 | 0.9868 |  | 6.2088 |  | 2.6386 |  | 31.6316 | #DIV/0! | #DIV/0! |  |  | 42.4977 | #DIV/0! | #DIV/0!
4 | 1.0212 |  | 6.4198 |  | 2.7313 |  | 31.6767 | #DIV/0! | #DIV/0! |  |  | #REF! | #DIV/0! | #REF!
5 | 1.004 |  | 5.8711 |  | 2.5495 |  | 31.754 | #REF! | #REF! |  |  | #REF! | #DIV/0! | #REF!
6 | 1.0018 |  | 7.5158 |  | 3.1259 |  | 32.6082 | #REF! | #REF!
Plant Cake | 0.9913 |  | 5.0174 |  | 2.2277 |  | 30.7096 | #DIV/0! | #DIV/0! |  |  | 44.3995 | #DIV/0! | #DIV/0!
Sludge | 0.9972 |  | 10.2122 |  | 1.316 |  | 3.4596 | #DIV/0! | #DIV/0! | 1.108 |  | 2.0368 | #DIV/0! | #DIV/0!
=
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Cake optimal | cake optimal (TS) | optimal cake | EPD determination | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EPD Manual Checked with Cake TS (lb/ton) | EPD Manual Cake TS (%) | EPD Manual Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%) | OPD Manual checked | EPD Manual checked
12.6805 | #DIV/0! | 120.8 | 32.0828 | 795 | #DIV/0! | #DIV/0! | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 |  | 120.8 |  |  |  | 19.3161 | 31.8388 | 640 | 19.3161 | 31.8388 | 640 | 0 |  |  | 32.0136 | 1 | 15.2225 | 32.0828 | 795 | 1000 | 795 |  | 1 | 15.2225 | 32.0828 | 795 | 0 |  | 23.8571 | 30.4793 | 375 | 3.5012
15.2225 | #DIV/0! | 73.1 | 22 | 675 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 96.95 | 24.6003 | 10 | 2 | [9 empty] | 0.33225 | 2 | [17 empty] | 1
17.2104 | #DIV/0! | 55.9 | 32.3333 | 640 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 64.5 | 13.3333 | 10 | 2 | [9 empty] | 31.6814 | 1 | [16 empty] | 1
19.3161 | #DIV/0! | 45.4 | 31.8388 | 550 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 50.65 | 10.3653 | 10 | 1 | [7 empty] | 1 | 31.8388 |  | 1
20.7962 | #DIV/0! | 38.1 | 31.8052 | 440 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 41.75 | 8.7425 | 10 | 2 | [7 empty] | 1 | 31.8052 |  | 1
21.7864 | 0 | 39.7 | 32.3968 | 440 | #DIV/0! | #DIV/0! | 10 | #DIV/0! | [8 empty] | 38.9 | -2.0566 | 10 | 2 | [7 empty] | 1 | 32.3968 |  | 1
1.0378
Haydee's calculations
is EPD cake TS < than OPD cake TS or higher?
[28 empty] | 31.9925 |  | 31.6968
[28 empty] | 0.29567 |  |  | 0.33225
[8 empty] | ` | [18 empty] | error% | 0.92419 | (<10% to have valid data for EPD determination)
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Power BI link to keep track of SBT3 TS Reply: https://app.powerbi.com/links/HmphV_SRql?ctid=8d05cdc4-bf69-4e6a-b5d3-428050a7f00f&pbi_source=linkShare&bookmarkGuid=8646a84a-93f8-4958-b225-6d1c00498ce5
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: During the testing, please use previous fe feed TS for decision making, Please make sure we use the measured valued in the same day to estimate the right polymer dose in lb/ton
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on N42: Parnia Behbahani (CTR): the color of supernatant for fist sample is dark.
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
Note on AE97: Hua G. Chieu (CTR): Average of all Cake TS after OPD point.
Note on AE98: Hua G. Chieu (CTR): Stdev of all Cake TS after OPD point.
Note on AE99: Hua G. Chieu (CTR): If stdev < 10% error, then optimal cake TS = avg - stdev of the cake TS after OPD point
Note on AE103: Hua G. Chieu (CTR): % error of stdev

## 05_28_2020
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/28/2024
Plant Data Conversion |  |  |  |  | Summary Table
Belt No. | A4 | Poly Loading (lb) | 448.8288 |  |  |  |  | batch testing
Poly Ratio | 0.165 | Floc Poly Flow (gpm) | 14.949 |  |  | unit | Plant | OPD | EPD
Sludge Flow (gpm) | 90.6 | Poly Floc Flow (mgd) | 0.021527 |  | BFP TS | %TS | 3.5085
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.13046 |  | Polymer ratio setting | - | 0.165 | 0.165 | 0.165
SBT3 TS % LAB_TSPCT_J04 | 6.1 | Calculated BFP TS (%) | 3.7289 |  | Polymer dose | lb/tonTS | 21.7109 | 26.6031 | 23.8997
BFP TS % | 3.7999 | BFP Sludge Loading (dtpd) | 20.2865 |  | Cake TS | %TS | 28.6677 | 26.0874 | 29.7472
DIG SLDG FLOW FROM SBT (gpm) | 552 | Plant Polydose (Ib/ton) - method 1 | 22.1245 |  | Filtrate TSS | mg TSS/L | 600 | 810 | 705
DIL WTR FLOW TO BFP (gpm) | 351 | Plant Polydose (Ib/ton) - method 2 | 21.7109
Assumptions and Constants:
1 g = | 0.0022046 | lb
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches
Cup Area: | 0.0079059 | m2
Aiming for 0.80 kg of DS per m2 of cup area
Cup Loading | 6.3247 | grams of DS
Assuming | 3.5 | TS in sludge
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m
Calculation
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g)
1 | 17 | 3.8 | 504.72 | 65.2098 | 67.24 | 1.98 | 65.26 | 17.0131 | 206.64 | 408.48 | 351.96 | 786.95 | 100 | 145.32 | 378.47 | 12.1285 | 52.1477
2 | 19 | 3.8 | 503.8 | 72.7487 | 73.85 | 2.11 | 71.74 | 18.7366 | 205.76 | 407.97 | 353.89 | 795.38 | 100 | 148.13 | 387.41 | 12.0258 | 52.5928
3 | 21.5 | 3.8 | 501.37 | 81.9238 | 83.5 | 1.9 | 81.6 | 21.415 | 159.38 | 412.95 | 301.78 | 785.76 | 100 | 142.4 | 372.81 | 11.8242 | 53.4899
4 | 24 | 3.8 | 502.76 | 91.7034 | 92.92 | 1.6 | 91.32 | 23.8997 | 401.68 | 399.01 | 540.86 | 759.18 | 100 | 139.18 | 360.17 | 11.5379 | 54.8168
5 | 26.5 | 3.8 | 500.98 | 100.8973 | 102.91 | 1.62 | 101.29 | 26.6031 | 509.76 | 686.52 | 684.82 | 1047 | 100 | 175.06 | 360.48 | 9.6698 | 65.4069
6 | 29 | 3.8 | 504.06 | 111.0948 | 112.85 | 1.22 | 111.63 | 29.1397 | 443.26 | 361.64 | 571.18 | 741 | 100 | 127.92 | 379.36 | 12.3371 | 51.2659
CST Table | [16 empty] | 0
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 121.6 | 47.9667 |  |  | 128.9 | 114.3 |  | 42.7 | 54.6 | 46.6
2 | 114.4333 | 45.05 | 91.6 | 133 | 118.7 |  |  | 41.8 |  | 48.3
3 | 55.6 | 43.9333 |  | 52.7 | 58.5 | 65 |  | 42.9 | 39.7 | 49.2 | [9 empty] | Summary - 05 - 03 - 2024 | [7 empty] | Trend over time
4 | 49.2 | 39.8 | 54.4 | 44 |  |  | 67 | 37.7 | 37.1 | 44.6
5 | 40.55 | 34.05 | 42.1 | 41.7 | 39.4 |  |  | 33.1 |  | 35 |  | 43.7
6 | 39.8333 | 24.0333 | 39 | 41 | 39.5 |  |  | 28.7 | 22.4 | 21
TSS - VSS | [23 empty] | BFP TS | Filtrate TS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%) | [7 empty] | Unit | % | mg TSS/L
1 | 1.0936 | 1.0981 | 10 | 10 | 1.105 | 1.1105 | 1 | 1.14 | 1.24 | 1.19 | 1.0952 | 1.1002 | 980 | 1030 | 1005 | [8 empty] | 3 - 3.9 | <= 812
2 | 1.1015 | 1.1064 | 10 | 10 | 1.1126 | 1.1182 | 1 | 1.11 | 1.18 | 1.145 | 1.1024 | 1.1084 | 1020 | 980 | 1000
3 | 1.1183 | 1.12 | 10 | 10 | 1.127 | 1.131 | 1 | 0.87 | 1.1 | 0.985 | 1.1185 | 1.122 | 850 | 900 | 875 | [5 empty] | Summary Table
4 | 1.1297 | 1.1231 | 10 | 10 | 1.1364 | 1.1305 | 1 | 0.67 | 0.74 | 0.705 | 1.1303 | 1.1242 | 610 | 630 | 620 | [8 empty] | batch testing
5 | 1.1131 | 1.1171 | 10 | 10 | 1.1213 | 1.1251 | 1 | 0.82 | 0.8 | 0.81 | 1.1134 | 1.1179 | 790 | 720 | 755 | [6 empty] | unit | Plant | OPD | EPD
6 | 1.1061 | 1.1164 | 10 | 10 | 1.1103 | 1.1207 | 1 | 0.42 | 0.43 | 0.425 | 1.1065 | 1.1169 | 380 | 380 | 380
Plant Filterate | 1.102 | 1.1056 | 10 | 10 | 1.1079 | 1.1134 | 1 | 0.59 | 0.78 | 0.685 | 1.1022 | 1.1071 | 570 | 630 | 600 | [5 empty] | BFP TS | %TS | 3.5085
. | [20 empty] | Polymer ratio setting | vol/vol | 0.165 | 0.165 | 0.165
[21 empty] | Polymer dose | lb/tonTS | 21.7109 | 26.6031 | 23.8997
TS - VS | [20 empty] | Cake TS | %TS | 28.6677 | 26.0874 | 29.7472
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%) | [6 empty] | Filtrate TSS | mg TSS/L | 600 | 810 | 705
1 | 0.9859 | 0.9891 | 5.07 | 5.1332 | 2.1986 | 2.2118 | 29.6932 | 29.5046 | 29.5989 | 1.4211 | 1.428 | 15.3353 | 15.2692 | 15.3023
2 | 0.9919 | 0.9909 | 5.1155 | 5.1928 | 2.174 | 2.1693 | 28.6667 | 28.0445 | 28.3556 | 1.4224 | 1.4178 | 14.6926 | 14.472 | 14.5823
3 | 1.0131 | 0.9908 | 5.058 | 5.504 | 2.152 | 2.3096 | 28.1564 | 29.221 | 28.6887 | 1.431 | 1.4774 | 14.2546 | 15.1199 | 14.6873
4 | 0.9809 | 0.9809 | 5.1914 | 5.1421 | 2.2377 | 2.2145 | 29.8492 | 29.6453 | 29.7472 | 1.4405 | 1.4358 | 15.3562 | 15.1436 | 15.2499
5 | 0.9794 | 0.9999 | 5.2653 | 5.1175 | 2.1164 | 2.0559 | 26.5289 | 25.646 | 26.0874 | 1.3894 | 1.3804 | 13.8074 | 13.1998 | 13.5036
6 | 0.9806 | 0.9845 | 5.1728 | 5.0518 | 2.2263 | 2.1789 | 29.7147 | 29.3659 | 29.5403 | 1.4311 | 1.4147 | 15.3727 | 15.1273 | 15.25
Plant Cake | 0.9868 | 0.9974 | 5.2389 | 5.0126 | 2.2032 | 2.1509 | 28.607 | 28.7283 | 28.6677 | 1.4345 | 1.425 | 14.6729 | 14.4815 | 14.5772
Sludge | 1.0107 | 1.0055 | 5.2604 | 5.0626 | 1.1589 | 1.1487 | 3.4873 | 3.5296 | 3.5085 | 1.0619 | 1.0559 | 1.844 | 1.8331 | 1.8385
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Note: Based on Sludge | Ave | Diff | Tolerance (%) | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%)
17.0131 | 47.9667 | 121.6 | 29.5989 | 1190 | 47.9667 | 0 | 20 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 121.6 | 0 | 20 | 2 | 26.6031 | 26.0874 | 810 | 26.6031 | 26.0874 | 810 |  | 29.5989 | 0 | 20 | 2 | 18.7366 | #N/A | #N/A | 812 | #N/A |  | #N/A | 23.8997 | 29.7472 | 705 | yes |  | 21.7109 | 28.6677 | 600 | 3.5085
18.7366 | 45.05 | 114.4333 | 28.3556 | 1145 | 46.5083 | 6.0806 | 20 | 2 | [8 empty] | 118.0167 | 5.8936 | 20 | 2 | [7 empty] | 28.9772 | 4.2006 | 20 | 2
21.415 | 43.9333 | 55.6 | 28.6887 | 985 | 44.4917 | 5.5366 | 20 | 2 | [8 empty] | 85.0167 | 52.888 | 20 | 2 | [7 empty] | 28.5221 | 0.99575 | 20 | 2
23.8997 | 39.8 | 49.2 | 29.7472 | 705 | 41.8667 | 10.545 | 20 | 2 | [8 empty] | 52.4 | 42.129 | 20 | 2 | [7 empty] | 29.218 | -4.2953 | 20 | 2
26.6031 | 34.05 | 40.55 | 26.0874 | 810 | 36.925 | 18.6704 | 20 | 2 | [8 empty] | 44.875 | 22.6145 | 20 | 1 | [7 empty] | 27.9173 | 10.7144 | 20 | 2
29.1397 | 24.0333 | 39.8333 | 29.5403 | 425 | 29.0417 | 34.9131 | 20 | 2 | [8 empty] | 40.1917 | 11.2349 | 20 | 2 | [7 empty] | 27.8139 | -5.8135 | 20 | 2
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on D32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sub-sample weight
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 readings
Note on I41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 reading Extra slots are given for outliers
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
OPD
EPD

## 05_21_2020
General guidelines:
fill in blue cells
other cells are calculated
Bench Scale Dewatering test Summary - 05/21/2024
Summary Table
Belt No. | A3 | Poly Loading (lb) | 415.0428 |  |  |  |  | batch testing
Poly Ratio | 0.177 | Floc Poly Flow (gpm) | 13.8237 |  |  | unit | Plant | OPD | EPD
Sludge Flow (gpm) | 78.1 | Poly Floc Flow (mgd) | 0.019906 |  | BFP TS | %TS | 3.7999
Polymer sol. | 0.25 | Sludge Flow(mgd) | 0.11246 |  | Polymer ratio setting | - | 0.177 | 0.177 | 0.177
SBT3 TS % LAB_TSPCT_J04 | 6.1 | Calculated BFP TS (%) | 3.4892 |  | Polymer dose | lb/tonTS | 25.9531 | 32.7416 | 23.6205
BFP TS % | 3.41 | BFP Sludge Loading (dtpd) | 16.3637 |  | Cake TS | %TS | 28.9719 | 29.7349 | 32.8894
DIG SLDG FLOW FROM SBT (gpm) | 282 | Plant Polydose (Ib/ton) - method 1 | 25.3636 |  | Filtrate TSS | mg TSS/L | 580 | 335 | 835
DIL WTR FLOW TO BFP (gpm) | 211 | Plant Polydose (Ib/ton) - method 2 | 25.9531
Assumptions and Constants:
1 g = | 0.0022046 | lb
1 g = | 1.1023e-06 | ton
Cup Diameter | 3.95 | inches
Cup Area: | 0.0079059 | m2
Aiming for 0.80 kg of DS per m2 of cup area
Cup Loading | 6.3247 | grams of DS
Assuming | 3.5 | TS in sludge
Assuming 100% Capture in free drainage
Polymer Solution | 0.25
Plains Target DS | 4 to 7 | kg DS/m
Calculation
Sample # | Polymer Dose (lb polymer/ ton sludge) | Actual Belt Filter Press before PD TS (%) | Sludge Weight (g) | Calculation Polymer Added(g) | Polymer Before (g) | Poymer after (g) | Actual Polymer Added (g) | Actual Polymer Added (lb/ton) | Sieve Weight (g) | Bucket Weight (g) | Sieve + Wet Solids Weight (g) | Bucket + Filtrate (g) | Capture Efficiency (%) | Filtered Solids (g) | Filtrate (g) | Estimated TS% of Wet Solids on frabic | Target WS in Cup (g)
1 | 19.5 | 3.41 | 500.54 | 66.5668 | 70.28 | 1.98 | 68.3 | 20.0077 | 206.78 | 409.17 | 347.93 | 779.21 | 100 | 141.15 | 370.04 | 10.8669 | 58.2019
2 | 23 | 3.41 | 503.13 | 78.9209 | 83.55 | 2.5 | 81.05 | 23.6205 | 205.82 | 408.9 | 347.35 | 782.64 | 100 | 141.53 | 373.74 | 10.6924 | 59.1517
3 | 26 | 3.41 | 509.78 | 90.3942 | 97.51 | 2.74 | 94.77 | 27.2586 | 159.42 | 408.25 | 295.74 | 827.41 | 100 | 136.32 | 419.16 | 11.7169 | 53.9794
4 | 28.5 | 3.41 | 506.6 | 98.4678 | 103.21 | 1.7 | 101.51 | 29.3805 | 401.84 | 359.01 | 550.82 | 771.74 | 100 | 148.98 | 412.73 | 10.7108 | 59.05
5 | 31.5 | 3.41 | 502.02 | 107.8489 | 116.12 | 4.02 | 112.1 | 32.7416 | 509.78 | 399.07 | 675.12 | 810 | 100 | 165.34 | 410.93 | 9.7156 | 65.0985
| 35 | 3.41 | 500.45 | 119.4574 | 120.24 | 1.12 | 119.12 | 34.9012 | 401.84 | 359.01 | 558.54 | 808.95 | 101 | 156.7 | 449.94 | 10.6632 | 59.3137
CST Table | [16 empty] | 0
Sample # | CST Sludge (Avrg) | CST Supernatant (Avrg) | CST Sludge |  |  |  |  | CST Supernatant
1 | 73.2333 | 39.5333 | 73.6 | 70.2 | 75.9 |  |  | 39.9 | 39 | 39.7
2 | 48 | 37.4 | 48.1 | 48.7 | 47.2 | 36.6 |  | 42.2 | 38.2 | 36.6
3 | 46.8333 | 31.05 | 50.2 | 44.7 | 45.6 | 37.4 |  | 31.3 | 31.4 | 30.7 | [9 empty] | Summary - 05 - 03 - 2024 | [7 empty] | Trend over time
4 | 37.7333 | 28.4 | 38.4 | 38.6 | 36.2 | 32.4 |  | 27.1 | 28.8 | 29.3
5 | 28.2333 | 15.8 | 28.3 | 27.3 | 29.1 | 19.8 |  | 22.1 | 12.8 | 12.5
6 | 28.6 | 12 | 27.3 | 29.7 | 28.8 | 19.6 |  | 11.8 | 11.7 | 12.5
Target table
TSS - VSS | [23 empty] | BFP TS | Filtrate TS
Sample ID/# | Foil Tray+Filter Weight (g ) #1 | Foil Tray+Filter Weight (g ) #2 | Sample Volume (ml) #1 | Sample Volume (ml) #2 | After 103 °C #1 | After 103 °C #2 | Dilution Factor | TSS-1 | TSS-2 | TSS (g TSS/L) | After 550 °C #1 | After 550 °C #2 | VSS-1 (%) | VSS-2 (%) | VSS (%) | [7 empty] | Unit | % | mg TSS/L
1 | 1.1038 | 1.1116 | 10 | 10 | 1.1137 | 1.1225 | 1 | 0.99 | 1.09 | 1.04 | 1.1085 | 1.1138 | 520 | 870 | 695 | [8 empty] | 3 - 3.9 | <= 812
2 | 1.1345 | 1.1268 | 10 | 10 | 1.1422 | 1.1358 | 1 | 0.77 | 0.9 | 0.835 | 1.136 | 1.1286 | 620 | 720 | 670
3 | 1.114 | 1.1224 | 10 | 10 | 1.1231 | 1.1285 | 1 | 0.91 | 0.61 | 0.76 | 1.116 | 1.1233 | 710 | 520 | 615 | [5 empty] | Summary Table
4 | 1.1174 | 1.115 | 10 | 10 | 1.1213 | 1.119 | 1 | 0.39 | 0.4 | 0.395 | 1.1179 | 1.1148 | 340 | 420 | 380 | [8 empty] | batch testing
5 | 1.1218 | 1.1165 | 10 | 10 | 1.1253 | 1.1197 | 1 | 0.35 | 0.32 | 0.335 | 1.1217 | 1.1168 | 360 | 290 | 325 | [6 empty] | unit | Plant | OPD | EPD
6 | 1.1181 | 1.1172 | 10 | 10 | 1.122 | 1.121 | 1 | 0.39 | 0.38 | 0.385 | 1.1181 | 1.1178 | 390 | 320 | 355
Plant Filterate | 1.1103 | 1.1087 | 10 | 10 | 1.1169 | 1.1154 | 1 | 0.66 | 0.67 | 0.665 | 1.111 | 1.1097 | 590 | 570 | 580 | [5 empty] | BFP TS | %TS | 3.7999
. | [20 empty] | Polymer ratio setting | vol/vol | 0.177 | 0.177 | 0.177
[21 empty] | Polymer dose | lb/tonTS | 25.9531 | 32.7416 | 23.6205
TS - VS | [20 empty] | Cake TS | %TS | 28.9719 | 29.7349 | 32.8894
Sample ID/# | Foil Tray (g) #1 | Foil Tray (g) #2 | Tray +Sample (g) #1 | Tray + Sample (g) #2 | After 103 °C #1 | After 103 °C #2 | TS-1 (%) | TS-2 (%) | TS (%) | After 550 °C #1 | After 550 °C #2 | VS-1 (%) | VS-2 (%) | VS (%) | [6 empty] | Filtrate TSS | mg TSS/L | 580 | 335 | 835
1 | 1.0061 | 1.0124 | 5.2952 | 5.3098 | 2.2718 | 2.3265 | 29.5097 | 30.579 | 30.0443 | 1.4507 | 1.4722 | 15.5065 | 16.0891 | 15.7978
2 | 1.0114 | 1.0056 | 5.2581 | 5.1396 | 2.417 | 2.3566 | 33.0986 | 32.6802 | 32.8894 | 1.5103 | 1.4837 | 17.2439 | 16.9838 | 17.1138
3 | 0.9888 | 1.0072 | 5.2674 | 5.4188 | 2.3317 | 2.306 | 31.3864 | 29.4406 | 30.4135 | 1.4618 | 1.4598 | 16.5148 | 15.616 | 16.0654
4 | 1.004 | 0.9975 | 5.0896 | 5.3244 | 2.2401 | 2.3258 | 30.255 | 30.6987 | 30.4768 | 1.4349 | 1.4602 | 15.8205 | 16.2572 | 16.0389
5 | 1.0014 | 0.9955 | 5.0068 | 5.5062 | 2.2412 | 2.2818 | 30.9532 | 28.5166 | 29.7349 | 1.4295 | 1.44 | 16.212 | 15.2882 | 15.7501
6 | 1.0062 | 0.996 | 5.0685 | 5.1949 | 2.2471 | 2.226 | 30.5467 | 29.2934 | 29.9201 | 1.4378 | 1.4217 | 15.9672 | 15.4825 | 15.7249
Plant Cake | 1.0041 | 0.9928 | 5.3082 | 5.1555 | 2.297 | 2.1544 | 30.0388 | 27.905 | 28.9719 | 1.443 | 1.3901 | 16.0883 | 14.8249 | 15.4566
Sludge | 1.0059 | 0.9798 | 5.0524 | 5.1096 | 1.1594 | 1.137 | 3.7934 | 3.8065 | 3.7999 | 1.0616 | 1.0413 | 1.9357 | 1.8729 | 1.9043
Actual Polymer Added (lb/ton) | CST Supernatant (second) | CST Sludge (second) | Lab Cake TS (%) | Lab Filtrate TSS (mg TSS/L) | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Manual check | Note: Based on Supernatant | Ave | Diff | Tolerance (%) | 1 or 2 | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | OPD (lb/ton) | OPD Cake TS (%) | OPD Filtrate TSS (mg TSS/L) | Note: Based on Sludge | Ave | Diff | Tolerance (%) | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Target Fiftrate TSS (mg TSS/L) | EOPD checked with Filtrate TSS (lb/ton) | Check filtrate condition | 1 or 2 | EOPD Checked with Cake TS (lb/ton) | EOPD Cake TS (%) | EOPD Filtrate TSS (mg TSS/L) | Manual check (yes/No) | Note | Grab Plant PD (lb/Ton) | Plant Cake TS (%) | Plant Filtrate (mg TSS/L) | Lab DW Feed TS (%)
20.0077 | 39.5333 | 73.2333 | 30.0443 | 1040 | 39.5333 | 0 | 20 | 2 | 34.9012 | 29.9201 | 385 | 34.9012 | 29.9201 | 385 |  |  | 73.2333 | 0 | 20 | 2 | 32.7416 | 29.7349 | 335 | 32.7416 | 29.7349 | 335 |  | 30.0443 | 0 | 20 | 2 | 23.6205 | #N/A | #N/A | 812 | #N/A |  | #N/A | 23.6205 | 32.8894 | 835 | yes |  | 25.9531 | 28.9719 | 580 | 3.7999
23.6205 | 37.4 | 48 | 32.8894 | 835 | 38.4667 | 5.3963 | 20 | 2 | [8 empty] | 60.6167 | 34.4561 | 20 | 2 | [7 empty] | 31.4669 | -9.4697 | 20 | 2
27.2586 | 31.05 | 46.8333 | 30.4135 | 760 | 34.225 | 19.2808 | 20 | 2 | [8 empty] | 47.4167 | 22.7385 | 20 | 2 | [7 empty] | 31.6515 | 3.3476 | 20 | 2
29.3805 | 28.4 | 37.7333 | 30.4768 | 395 | 29.725 | 17.0197 | 20 | 2 | [8 empty] | 42.2833 | 20.4218 | 20 | 2 | [7 empty] | 30.4452 | 3.7111 | 20 | 2
32.7416 | 15.8 | 28.2333 | 29.7349 | 335 | 22.1 | 46.8461 | 20 | 2 | [8 empty] | 32.9833 | 33.2282 | 20 | 1 | [7 empty] | 30.1059 | 2.3329 | 20 | 2
34.9012 | 12 | 28.6 | 29.9201 | 385 | 13.9 | 45.7014 | 20 | 1 | [8 empty] | 28.4167 | 13.2895 | 20 | 2 | [7 empty] | 29.8275 | 0.61724 | 20 | 2
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red highlighted value comes from plant data conversion table
Note on D32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sub-sample weight
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 readings
Note on I41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take min 3 reading Extra slots are given for outliers
Note on D50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample volume will remain same unless need to change due to thickness of filtrate
Note on D61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sample + Tray weight >= 5g
OPD
EPD